## Cost Matrix - Updated (NEW)
Joint Utilities of New York - Technical Guidance Cost Matrix for Integrating DER - Updated and Combined
|  |  | NYSEG/ RGE | Central Hudson | Consolidated Edison | National Grid | Orange and Rockland
| Distribution Line Upgrades | Conductor upgrade/Reconductoring (open wire - Spacer) | $350,000-$550,000 per mile depending on voltage and not including tree work | $/mile for three-phase reconductoring or line extension $500,000-$800,000 | Install/remove one mile of open wire 1/0 Al bare primary, crossarm construction with 25% pole replacements and transfer associated equipment and secondary/neutral $1,056,000 | Replace one mile of existing smaller gauge primary conductor with 366 Al bare primary, crossarm construction with 50% pole replacements and transfer associated equipment and secondary/neutral $451,000 per mile | Install/remove one mile of open wire 477MCM ACSR primary, crossarm construction with 25% pole replacements and transfer associated equipment and secondary/neutral O&R – $/mile. No differentiation for line size or construction. Does not include tree trimming $665,280
|  | New Overhead Line extension | $275,000 not including tree work | $/mile for three-phase reconductoring or line extension $500,000-$800,000 | Install one mile of open wire 1/0 Al bare primary, crossarm construction with associated equipment and neutral $1,640,500 | Install one mile of open wire 477 Al bare primary, crossarm construction with associated equipment and neutral $374,000 per mile | Install one mile of open wire 477MCM ACSR primary, crossarm construction with associated equipment and neutral O&R – $/mile. No differentiation for line size or construction. Does not include tree trimming $712,800
|  | Recloser upgrade/installation | Install 15kV 6IVS Viper recloser and bypass disconnects $75,000 | Installation of electronic recloser with disconnects and controls for 15kV interconnection $65,000-$75,000 | Install 15kV Recloser $162,000 | Install/Replace 15kV 6IVS viper recloser and bypass disconnects $67,000-$70,000 | Install 15kV recloser and bypass disconnects O&R – can provide. O&R uses Eaton reclosers. $80,000
|  |  | Install 35kV 6IVS Viper recloser and bypass disconnects $95,000 | Installation of electronic recloser with disconnects and controls for 35kV interconnection $65,000-$75,000 | N/A | Install 35kV 6IVS viper recloser and bypass disconnects N/A National Grid typically would not install a recloser on Sub-T unless it was part of an already existing sectionalizing scheme. | Install 35kV recloser and bypass disconnects O&R – can provide. O&R uses Eaton reclosers. $100,000
|  | Install Line Regulators | Install a 15 kV single phase regulator up to a bank of 333 kVA platform mounted regulators $65,000-$110,000 | New three-phase, bi-directional regulator with controls for 15kV interconnection $70,000-$80,000 | Install new wood pole and 15kV 167 kVA line regulator with bi-directional control and install/remove associated equipment $46,720 - $140,140 *Note the cost can vary based on site specific requirements (e.g. single vs three phase equipment) | Install single 76.2 kVA regulator up to a bank of 333 kVA platform mounted regulators $30,000-$130,000 | Install new 50’ pole and 15kV 167kVA line regulator with bi-directional control and install/remove associated equipment O&R - $ for voltage line regulator but will not differentiate by voltage class $65,000
|  |  | Install new 35kV up to 833 kVA line regulator with bi-directional control and install/remove associated equipment $260,000 | New three-phase, bi-directional regulator with controls for 35kV interconnection $70,000-$80,000 | N/A | Install platformed mounted 667 kVA regulators with 3 grounding transformers and bypass switches $521,000 | Install new 50’ pole and 35kV 333kVA line regulator with bi-directional control and install/remove associated equipment O&R - $ for voltage line regulator but will not differentiate by voltage class $65,000
|  | Installation of new service pole with 3-phase overhead transformer bank (per 100kVA) | N/A | New service requests with no native load and/or systems 300kW and above require customer-owned transformer N/A | 28000 | N/A Please reference PSC220 for service upgrades within National Grid. | O&R – only applies to DER less than 500kW. Over this is customer owned. N/A
|  | Installation of new pad-mount transformer and meter (per 100kVA) | N/A | New service requests with no native load and/or systems 300kW and above require customer-owned transformer N/A | 37500 | N/A Please reference PSC220 for service upgrades within National Grid. | O&R – only applies to DER less than 500kW. Over this is customer owned. N/A
|  | Upgrade of existing overhead/pad-mounted service transformers | N/A | New service requests with no native load and/or systems 300kW and above require customer-owned transformer N/A | 24700 | N/A Please reference PSC220 for service upgrades within National Grid. | O&R – only applies to DER less than 500kW. Over this is customer owned. N/A
|  | Install new 1P capacitor bank (fixed/switched) (per 100kVAR) | $19,000/$50,000 varies depending on size and voltage | Central Hudson's standard design is three-phase capacitor banks N/A | 26000 | Install a new 1- Phase fixed bank capacitor with pole replacement and transfer associated equipment $5,000 | N/A
|  | Install new 3P capacitor bank (fixed/switched) (per 100kVAR) | $19,000/$50,000 varies depending on size and voltage | New three-phase switched capacitor bank with controls $25,000-$35,000 | 26000 | Install a new 3- Phase switched bank capacitor (300/600/900 KVAr) with pole replacement and transfer associated equipment $40,162/$40,614/$41,073 | O&R – Cost is for 3 phase RTU cap bank. Do not differentiate by size. $40,700
| Substation Upgrades | 3V0 installation | $573,000 Varies with voltage and scope | Install substation high-side potential transformer (PT) and relaying; Limited field implementation and substations that require 3V0 $90,000-$110,000 | Already in Con Edison design | Install voltage transformers on high-side substation transformer $567,000 National Grid is currently reviewing and updating estimates associated with 3V0 installation. This cost is subject to change. | Install voltage transformer on high-side substation transformer and install relay and wire to breakers. $372,738 - $479,460 Average +/- (1) standard deviation
|  | DTT Installation | $100,000 - $300,000 Does not include fiber run | Utilizing cellular based technology where low speed tripping is acceptable and PCC electronic recloser is already separately required $3,000-$10,000 | Soft Transfer Trip $40,000 - $100,000 | Install 1 DTT communication relay in the control house or outdoor cabinet $410,000 | Install 1 DTT communication relay in the control house or outdoor cabinet O&R - non typical N/A
|  | Install/Remove Regulators | Install and Remove 3-333kVA substation regulators and associated equipment $150,000 - $250,000 | Substation Regulator Upgrade (non - LTC) - limited number of substations that require full regulator replacement $100,000-$140,000 | N/A | N/A National Grid does not install within the fence regulators within New York | Install and Remove 3-333kVA substation regulators and associated equipment O&R – N/A. no substation regulators only LTC. N/A
|  | Upgrade to Bi-Directional Regulator Control | Install Bi-Directional regulator controls and remove existing controls $65,000 | See cost associated with Install/Remove Regulators or Upgrade substation transformer LTC N/A | N/A | Replace regulator(s) with bi-directional controls $30,000 - $130,000 | Install Bi-Directional regulator controls and remove existing controls Typically, bi-directionality is already available N/A
|  | Upgrade substation transformer LTC | 47000 | Setting changes up to controller replacements $15,000-$60,000 | LTC or substation regulator upgrade $240,000 per transformer | N/A | O&R - non typical N/A
|  | Reconductor underground feeder getaway | N/A | Central Hudson's standard design is overhead construction N/A | N/A | Upgrade substation getaway cable to 1000MCM CU, may or may not require conduit replacement. $ / foot assumed cable and concrete encased conduit run. Costs for upgrade are site specific. Current $ /ft is based on actual costs as of 7/28/22 and subject to change. $600-800/ft | O&R: $ / foot for substation UG exit. (site specific) $300-450/ft
| PCC Upgrades | Overhead (OH) Point of Interconnection (POI)/Point of Common Coupling (PCC) | Install approximately 160’ of 3 phase 477 conductor, 4 poles, 15kV recloser, 15 kV loadbreaks switch, 15kV primary meter, and miscellaneous overhead equipment. $145,000 | New Primary Metered Service - Install new pole (for take-off) and three-phase primary meter cluster on customer-owned pole; does not include cost for electronic recloser, see M&C section for size applicability and cost $15,000-$25,000 | Install approximately 160’ of 3 phase 1/0 AL conductor, 4 poles, 15kV recloser, 15 kV loadbreaks switch, 15kV primary meter, and miscellaneous overhead equipment $268,100 | Install approximately 160’ of 3 phase 1/0 AL conductor, 4 poles, 15kV recloser, 15 kV loadbreaks switch, 15kV primary meter, and miscellaneous overhead equipment $105,000 | Install approximately 160’ of 3 phase 477ACSR conductor, 4 poles, 15kV Power Quality metering, 15kV recloser, 15 kV loadbreak / bypass switches, 15kV primary meter, and miscellaneous overhead equipment. O&R – Scope is typically Install approximately 160’ of 3 phase 477ACSR conductor, 4 poles, 15kV Power Quality metering, 15kV recloser, 15 kV loadbreak / bypass switches, 15kV primary meter, and miscellaneous overhead equipment. $153,540
|  | Underground (UG) Point of Interconnection (POI)/Point of Common Coupling (PCC) | N/A | Central Hudson's standard design is overhead construction N/A | N/A | Install Approximately 100’ of 3-phase 4/0 AL UG cable, Padmounted 15 kV recloser, and 15 kV loadbreak switch $210,000 | N/A
|  | Single Phase, self-contained meter (600 V) | N/A | Three-phase required for systems > 50kW N/A | N/A | N/A Unaware that National Grid has received this request within New York. Please reference PSC220 for meter/service upgrades | O&R – N/A non-residential systems are 3 phase
|  | Secondary Metering | 2500 | Systems 300kW and greater require primary metering N/A | 1900 | N/A Unaware that National Grid has received this request within New York. Please reference PSC220 for meter/service upgrades | O&R – Only applicable to DER < 500kW $5,000
| Non-System Costs | Change settings (protection, regulator, cap) | N/A | Varies based on scope of work and identified within sections throughout as applicable N/A | Cost to upgrade each underground network protector relay settings. $2,600 *Does not include cost of equipment | National Grid costs for creating, updating, testing, and initializing settings for use $5,000 | O&R – depends on scope of work N/A
|  | EMS Integration | N/A | Included within costs for M&C, refer to M&C section N/A | $6,000-$100,000 | Standalone Remote Terminal Unit (RTU) Equipment at Customer location with EMS integration - Install 1 Remote Terminal Unit Cabinet with Router, communications processor, enclosure heater, terminal blocks, AC/DC power converter, battery, temperature sensor and grounding kit. $66,000 The Interconnection Customer (IC) will be responsible for all initial and recurring costs associated with communications for the RTU. Such costs are not explicitly represented in the total above. | O&R – N/A with customer owned DER equipment. Included in recloser costs above.
| Telemetry | Overhead SCADA Recloser | N/A | Included within costs for M&C, refer to M&C section N/A | SCADA Only $6,000 | 105000 | O&R – Included in recloser cost above. N/A
|  | Underground SCADA Switch | N/A | Central Hudson's standard design is overhead construction N/A | Equipping SCADA to Network Protectors $20,000 - $100,000 for SCADA monitoring. Additional costs could be required depending on additional technical issues and re-configurations upon CESIR evaluation. | 210000 | O&R – N/A
| Monitoring and Control | M&C equipment for PV projects 50 kW - 500 kW | N/A | Based on estimates, no field implementation to date unless point of common coupling (PCC) electronic recloser required $21,000-$40,000 | $20,000 - $100,000 | N/A | If required - SCADA Monitoring/ Power Quality Meter - $40,000
|  | M&C equipment for PV projects 500 kW and greater | N/A | PCC electronic recloser with communications and controls $65,000-$75,000 | $20,000 - $100,000 for SCADA monitoring. Additional costs could be required depending on additional technical issues and re-configurations upon CESIR evaluation. | PCC Recloser with SCADA $105,000 | SCADA Monitoring/Power Quality Meter - $40,000 Control is via a recloser for projects typically 500kW and larger. $98,000
| Anti-Islanding Mitigation | Reclose blocking for mid-line reclosers | N/A | Setting changes up to new electronic recloser installation $1,000 - $75,000 | NA | Settings changes up to new mid line recloser installation/replacement $5,000- $70,000 | N/A
|  | Reclose blocking on substation breaker | N/A | For single phase feeder PT installations $25,000 | NA | N/A | N/A