## Instructions
Overview of tabs in excel file
Cost Guide Tables: The tables that are referenced in the Transmission Cost Estimation Guide.
Exploratory cost estimate tab: User enters in all the scopes of work for the potential project.
Line and substation exploratory example tabs: Provides details of example line and substation calculations.
Costs over time estimate tab: Estimated life-cycle costs for the first 20 years of project in-service are calcuated.
Convert to Nominal tab: Convert current year cost to "nominal" cost to construct using both an inflation faor and an estimated cash flow by year.
MISO Cost Estimation Guide for MTEP25
For more information and background on MISO's cost estimation approach, see MISO's Cost Estimation Guide for MTEP25 posted on MISO's website: http://www.misoenergy.org/planning/transmissionplanning
Disclaimer
This document is prepared for informational purposes only to support MISO planning staff in developing cost estimates and deriving benefit-to-cost ratios for solutions proposed for inclusion in the MISO Transmission Expansion Plan (MTEP). MISO’s cost estimation approach is based on staff experience, vendor consultation, industry practice, and stakeholder feedback. MISO makes every effort to develop its cost estimates from the most accurate and appropriate assumptions and information available at that time. However, MISO cannot and does not guarantee the accuracy of information, assumptions, judgments, or opinions contained herein or derived therefrom. MISO may revise or terminate this document at any time at its discretion without notice. MISO’s cost estimation assumptions are not an indication or a direction for how any particular project shall be designed or built.

## Cost Guide Tables
MISO Transmission Cost Estimation Guide - Supplemental Tables
For MTEP25
Table 2.1: Land Cost per acre
| State | Pasture | Crop | Urban/ Suburban | Acquisition | Regulatory & permitting
| Arkansas | 3400.8 | 10202.4 | 17004 | 14817.1535 | 3086.907
| Illinois | 4128.8 | 12386.4 | 20644 | 14817.1535 | 3086.907
| Indiana | 2776.8 | 8330.4 | 13884 | 14817.1535 | 3086.907
| Iowa | 3640 | 10920 | 18200 | 14817.1535 | 3086.907
| Kentucky | 3920.8 | 11762.4 | 19604 | 14817.1535 | 3086.907
| Louisiana | 3494.4 | 10483.2 | 17472 | 14817.1535 | 3086.907
| Michigan | 3088.8 | 9266.4 | 15444 | 14817.1535 | 3086.907
| Minnesota | 2298.4 | 6895.2 | 11492 | 14817.1535 | 10310.2693
| Mississippi | 3244.8 | 9734.4 | 16224 | 14817.1535 | 3086.907
| Missouri | 2756 | 8268 | 13780 | 14817.1535 | 3086.907
| Montana | 925.6 | 2776.8 | 4628 | 14817.1535 | 3086.907
| North Dakota | 1092 | 3276 | 5460 | 14817.1535 | 5155.1347
| South Dakota | 1320.8 | 3962.4 | 6604 | 14817.1535 | 4136.4553
| Texas | 2288 | 6864 | 11440 | 14817.1535 | 3086.907
| Wisconsin | 3328 | 9984 | 16640 | 14817.1535 | 10310.2693
Table 2.2-1: AC transmission - steel pole - single circuit
| Voltage class | 69 kV | 115 kV | 138 kV | 161 kV | 230 kV | 345 kV | 500 kV | 765 kV
Tangent structure
| Steel weight (lbs.) | 7000 | 7900 | 8400 | 9300 | 11100 | 22300 | 35100 | 52800
| Foundation size (Cu. Yd) | 5.5 | 6 | 8 | 9 | 13 | 21 | 41 | 60
| Material | 19252.1064 | 21727.3772 | 23102.5276 | 25577.7985 | 30528.3401 | 61331.7103 | 96535.5619 | 145217.1159
| Installation | 24927.8453 | 28132.854 | 29913.4143 | 33118.423 | 39528.4404 | 79412.9928 | 124677.3812 | 188026.1159
| Hardware | 4973.9859 | 5802.7828 | 6218.3859 | 7047.1828 | 8289.1734 | 11091.1815 | 12142.838 | 24365.1826
| Foundation | 8898.7246 | 9707.0425 | 12942.7233 | 14560.5638 | 21031.9254 | 33974.6488 | 66331.4571 | 97069.2204
Running angle structure
| Steel weight (lbs.) | 11600 | 13000 | 13900 | 15300 | 18300 | 37900 | 59700 | 149000
| Foundation size (Cu. Yd) | 9 | 10.5 | 13 | 14 | 19.5 | 30 | 54.5 | 85
| Material | 31903.4906 | 35753.9118 | 38229.1826 | 42079.6039 | 50330.5067 | 104236.4045 | 164192.9643 | 409798.519
| Installation | 41309.0007 | 46294.5698 | 49499.5785 | 54485.1475 | 65168.5098 | 134966.4766 | 212598.909 | 530603.8127
| Hardware | 4973.9859 | 5802.7828 | 6218.3859 | 7047.1828 | 8289.1734 | 11091.1815 | 12142.838 | 24365.1826
| Foundation | 14560.5638 | 16987.9267 | 21031.9254 | 22649.7658 | 31548.4905 | 48535.2125 | 88172.9051 | 137514.0262
Non-angled deadend structure
| Steel weight (lbs.) | 14000 | 15800 | 16800 | 18600 | 22200 | 42400 | 66700 | 154675
| Foundation size (Cu. Yd) | 11 | 12 | 15 | 16.5 | 22.5 | 33.5 | 60 | 160
| Material | 38504.2127 | 43454.7544 | 46205.0553 | 51155.5969 | 61056.6802 | 116612.7586 | 183445.0707 | 425406.4767
| Installation | 49855.6906 | 56265.7079 | 59826.8287 | 66236.846 | 79056.8807 | 150991.52 | 237526.7543 | 550813.173
| Hardware | 9807.0282 | 11441.7336 | 12259.6887 | 13893.1895 | 16345.8501 | 39865.3708 | 62710.2894 | 97460.7305
| Foundation | 17796.2446 | 19414.085 | 24267.6063 | 26694.9692 | 36402.0117 | 54198.2563 | 97070.425 | 258850.8528
Angled deadend structure
| Steel weight (lbs.) | 20400 | 23000 | 24500 | 27100 | 32400 | 48100 | 80700 | 154675
| Foundation size (Cu. Yd) | 15 | 16.5 | 20 | 21.5 | 29 | 41.5 | 72 | 160
| Material | 56106.1386 | 63256.9209 | 67382.3723 | 74533.1547 | 89109.7495 | 132289.4738 | 221949.2834 | 425406.4767
| Installation | 72646.8634 | 81905.7773 | 87247.4585 | 96506.3724 | 115380.3124 | 171289.9083 | 287382.4448 | 550813.173
| Hardware | 9807.0282 | 11441.7336 | 12259.6887 | 13893.1895 | 16345.8501 | 39865.3708 | 62710.2894 | 97460.7305
| Foundation | 24267.6063 | 26694.9692 | 32356.8083 | 34784.1713 | 46917.3721 | 67140.9796 | 116484.5101 | 258850.8528
Table 2.2-2: AC transmission – steel tower – single circuit
| Voltage class | 69 kV | 115 kV | 138 kV | 161 kV | 230 kV | 345 kV | 500 kV | 765 kV
Tangent structure
| Steel weight (lbs.) | 6100 | 6900 | 7300 | 8100 | 10100 | 20300 | 27000 | 34320
| Foundation size (Cu. Yd) | 8.5 | 11.5 | 13.5 | 14.5 | 15.5 | 19.5 | 33.5 | 39
| Material | 14005.6618 | 15842.4699 | 16760.874 | 18597.6821 | 23189.7024 | 46609.0057 | 61992.2736 | 94391.8006
| Installation | 18135.2194 | 20513.5393 | 21702.6993 | 24081.0192 | 30026.8191 | 60350.3982 | 80268.2977 | 122216.3924
| Hardware | 4973.9859 | 5802.7828 | 6218.3859 | 7047.1828 | 8289.1734 | 11091.1815 | 12142.838 | 24365.1826
| Foundation | 13752.2459 | 18605.7671 | 21841.448 | 23459.2884 | 25077.1288 | 31548.4905 | 54198.2563 | 63094.5716
Running angle structures
| Steel weight (lbs.) | 9200 | 10400 | 11000 | 12200 | 15200 | 30500 | 39800 | 89400
| Foundation size (Cu. Yd) | 16 | 19 | 19.5 | 22 | 24.5 | 39 | 72.5 | 81
| Material | 21123.2932 | 23878.5054 | 25256.1115 | 28011.3236 | 34899.354 | 70028.3091 | 91381.2034 | 245879.357
| Installation | 27350.6792 | 30918.1591 | 32701.8991 | 36269.379 | 45188.0787 | 90673.9773 | 118321.4166 | 318362.0757
| Hardware | 4973.9859 | 5802.7828 | 6218.3859 | 7047.1828 | 8289.1734 | 11091.1815 | 12142.838 | 24365.1826
| Foundation | 25885.4467 | 30738.9679 | 31548.4905 | 35592.4892 | 39637.6925 | 63095.7763 | 117294.0326 | 131042.6645
Non-angled deadend structure
| Steel weight (lbs.) | 10400 | 11700 | 12400 | 13800 | 17200 | 34500 | 45900 | 108273
| Foundation size (Cu. Yd) | 21.5 | 25 | 25.5 | 28.5 | 34 | 48.5 | 96 | 180
| Material | 23878.5054 | 26863.3186 | 28470.5257 | 31684.9399 | 39491.3743 | 79212.3496 | 105386.8652 | 297785.1476
| Installation | 30918.1591 | 34783.4589 | 36863.9589 | 41026.0188 | 51133.8785 | 102565.577 | 136456.636 | 385568.6912
| Hardware | 9807.0282 | 11441.7336 | 12259.6887 | 13893.1895 | 16345.8501 | 39865.3708 | 62710.2894 | 24365.1826
| Foundation | 34784.1713 | 40446.0104 | 41255.533 | 46109.0542 | 55006.5742 | 78465.8626 | 155312.6801 | 258850.8528
Angled deadend structure
| Steel weight (lbs.) | 13400 | 15200 | 16100 | 17800 | 22200 | 44700 | 59400 | 108273
| Foundation size (Cu. Yd) | 33.5 | 38 | 39 | 43 | 52 | 90 | 176 | 180
| Material | 30766.5358 | 34899.354 | 36965.7632 | 40868.9804 | 50971.425 | 102631.653 | 136383.002 | 297785.1476
| Installation | 39836.8589 | 45188.0787 | 47864.2186 | 52917.6185 | 65998.3781 | 132889.1561 | 176590.2549 | 385568.6912
| Hardware | 9807.0282 | 11441.7336 | 12259.6887 | 13893.1895 | 16345.8501 | 39865.3708 | 62710.2894 | 24365.1826
| Foundation | 54198.2563 | 61477.9359 | 63095.7763 | 69567.1379 | 84127.7017 | 145605.6376 | 284739.9135 | 258850.8528
Table 2.2-3: AC transmission – steel pole – double circuit
| Voltage class | 69 kV | 115 kV | 138 kV | 161 kV | 230 kV | 345 kV
Tangent structure
| Steel weight (lbs.) | 11300 | 12700 | 13500 | 14900 | 18600 | 36000
| Foundation size (Cu. Yd) | 8 | 10 | 14.5 | 17.5 | 23 | 46.5
| Material | 31078.4003 | 34928.8216 | 37129.0623 | 40979.4836 | 51155.5969 | 99010.8328
| Installation | 40240.6645 | 45226.2336 | 48075.1302 | 53060.6992 | 66236.846 | 128200.3471
| Hardware | 9682.9496 | 11297.176 | 12103.0846 | 13717.3111 | 16138.6508 | 21716.1647
| Foundation | 12942.7233 | 16178.4042 | 23459.2884 | 28312.8096 | 37210.3296 | 75230.1817
Running angle structures
| Steel weight (lbs.) | 15000 | 16800 | 17900 | 19700 | 24600 | 47700
| Foundation size (Cu. Yd) | 13 | 15.5 | 21.5 | 25.5 | 32.5 | 61
| Material | 41254.5137 | 46205.0553 | 49230.3863 | 54180.9279 | 67657.4024 | 131189.3534
| Installation | 53416.8113 | 59826.8287 | 63744.0615 | 70154.0788 | 87603.5705 | 169865.46
| Hardware | 9682.9496 | 11297.176 | 12103.0846 | 13717.3111 | 16138.6508 | 21716.1647
| Foundation | 21031.9254 | 25077.1288 | 34784.1713 | 41255.533 | 52580.4159 | 98688.2655
Non-angled deadend structure
| Steel weight (lbs.) | 16700 | 18700 | 19900 | 22000 | 27400 | 54000
| Foundation size (Cu. Yd) | 15.5 | 18.5 | 25 | 29.5 | 37 | 68.5
| Material | 45930.0252 | 51430.627 | 54730.9881 | 60506.62 | 75358.2449 | 148516.2491
| Installation | 59470.7166 | 66592.9581 | 70866.303 | 78344.6566 | 97574.7087 | 192300.5207
| Hardware | 19341.8062 | 22566.6452 | 24178.4624 | 27402.0968 | 32237.5483 | 79289.8409
| Foundation | 25077.1288 | 29930.65 | 40446.0104 | 47726.8946 | 59860.0954 | 110822.6709
Angled deadend structure
| Steel weight (lbs.) | 26000 | 29200 | 31100 | 34300 | 42800 | 84600
| Foundation size (Cu. Yd) | 20 | 24 | 32 | 37 | 46 | 81.5
| Material | 71507.8237 | 80308.7866 | 85534.3583 | 94335.3212 | 117712.8789 | 232675.457
| Installation | 92589.1396 | 103984.726 | 110750.8554 | 122146.4419 | 152415.9683 | 301270.8158
| Hardware | 19341.8062 | 22566.6452 | 24178.4624 | 27402.0968 | 32237.5483 | 79289.8409
| Foundation | 32356.8083 | 38828.17 | 51770.8934 | 59860.0954 | 74420.6592 | 131854.5963
Table 2.2-4: AC transmission – steel tower – double circuit
| Voltage class | 69 kV | 115 kV | 138 kV | 161 kV | 230 kV | 345 kV
Tangent structure
| Steel weight (lbs.) | 9200 | 10400 | 11000 | 12200 | 15200 | 36000
| Foundation size (Cu. Yd) | 13 | 17 | 19.5 | 21 | 22 | 31.5
| Material | 21123.2932 | 23878.5054 | 25256.1115 | 28011.3236 | 34899.354 | 82656.3648
| Installation | 27350.6792 | 30918.1591 | 32701.8991 | 36269.379 | 45188.0787 | 107024.3969
| Hardware | 9682.9496 | 11297.176 | 12103.0846 | 13717.3111 | 16138.6508 | 21716.1647
| Foundation | 21031.9254 | 27503.2871 | 31548.4905 | 33974.6488 | 35592.4892 | 50962.5755
Running angle structures
| Steel weight (lbs.) | 13800 | 15600 | 16500 | 18300 | 22800 | 53100
| Foundation size (Cu. Yd) | 22.5 | 28 | 34.5 | 37.5 | 46.5 | 59
| Material | 31562.1586 | 35817.7581 | 37884.1672 | 42016.9855 | 52349.0311 | 121918.1382
| Installation | 41026.0188 | 46377.2387 | 49053.3785 | 54404.5984 | 67782.1181 | 157861.5154
| Hardware | 9682.9496 | 11297.176 | 12103.0846 | 13717.3111 | 16138.6508 | 21716.1647
| Foundation | 36402.0117 | 45299.5317 | 55816.0967 | 60669.618 | 75230.1817 | 95452.5846
Non-angled deadend structure
| Steel weight (lbs.) | 16100 | 18200 | 19300 | 21400 | 26600 | 61200
| Foundation size (Cu. Yd) | 28.5 | 34.5 | 43 | 48.5 | 70.5 | 86.5
| Material | 36965.7632 | 41787.3845 | 44312.9956 | 49134.6169 | 61073.8696 | 140515.8202
| Installation | 47864.2186 | 54106.7785 | 57377.4983 | 63620.0582 | 79079.1377 | 181941.4748
| Hardware | 19341.8062 | 22566.6452 | 24178.4624 | 27402.0968 | 32237.5483 | 79289.8409
| Foundation | 46109.0542 | 55816.0967 | 69567.1379 | 78465.8626 | 114058.3517 | 139943.7984
Angled deadend structure
| Steel weight (lbs.) | 21200 | 23900 | 25300 | 28100 | 35000 | 79200
| Foundation size (Cu. Yd) | 43 | 50.5 | 61.5 | 68.5 | 99 | 125
| Material | 48675.4149 | 54874.6422 | 58089.0564 | 64517.8848 | 80360.3547 | 181844.0027
| Installation | 63025.4782 | 71052.8379 | 75214.8978 | 83539.0175 | 104051.497 | 235453.6733
| Hardware | 19341.8062 | 22566.6452 | 24178.4624 | 27402.0968 | 32237.5483 | 79289.8409
| Foundation | 69567.1379 | 81701.5434 | 99497.788 | 110786.5315 | 160166.2013 | 202230.0522
Table 2.2-5: AC transmission – wood pole – single circuit
| Voltage class | 69 kV | 115 kV | 138 kV | 161 kV | 230 kV
Tangent structure
| Material | 5412.1993 | 10130.6843 | 10257.149 | 13654.5073 | 14787.7786
| Installation | 13036.2456 | 13579.9524 | 15208.9532 | 21727.076 | 32590.614
| Hardware | 5186.0037 | 5865.4244 | 6420.7665 | 7100.1872 | 9261.3233
Running angle structures
| Material | 9502.0441 | 17745.5799 | 17933.4353 | 23911.6563 | 25862.6511
| Installation | 22813.4298 | 23791.6782 | 26616.1981 | 38022.383 | 57034.1045
| Hardware | 9075.8077 | 10249.1335 | 11236.9437 | 12409.0649 | 16237.4319
Angled deadend structure
| Material | 10823.1708 | 20325.2149 | 20514.298 | 27310.2425 | 29575.5573
| Installation | 26072.4912 | 27158.845 | 30417.9064 | 43454.1521 | 65181.2281
| Hardware | 10372.0074 | 11730.8488 | 12841.533 | 14200.3744 | 18521.4419
Table 2.2-6: AC transmission – wood pole – double circuit
| Voltage class | 69 kV | 115 kV
Tangent structure
| Material | 8936.0223 | 16738.7734
| Installation | 21509.8053 | 22432.941
| Hardware | 8581.9026 | 9692.5867
Running angle structures
| Material | 15668.1205 | 29260.0094
| Installation | 37641.8943 | 39271.9549
| Hardware | 15002.6691 | 16916.8526
Angled deadend structure
| Material | 17870.8169 | 33538.9373
| Installation | 43019.6105 | 44811.8293
| Hardware | 17462.5575 | 19386.3781
Table 2.2-7: HVDC transmission – steel pole – single circuit
| Voltage class | ± 250 kV | ± 400 kV | ± 500 kV | ± 600 kV | ± 640 kV
Tangent structure
| Steel weight (lbs.) | 14773 | 19943 | 21938 | 26325 | 54550
| Foundation size (Cu. Yd) | 17 | 23 | 26 | 31 | 63
| Material | 40715.5038 | 54965.5004 | 60462.4188 | 72555.1481 | 150028.9146
| Installation | 52719.4252 | 71170.4821 | 78287.4243 | 93945.757 | 194259.1371
| Hardware | 5390.7936 | 6866.4858 | 7468.8091 | 7830.2031 | 30457.0806
| Foundation | 27557.4962 | 37203.1017 | 41449.4811 | 49739.8591 | 101922.7416
Running angle structures
| Steel weight (lbs.) | 25126 | 33920 | 37313 | 44775 | 156450
| Foundation size (Cu. Yd) | 23 | 31 | 34 | 41 | 90
| Material | 69251.1035 | 93489.3581 | 102837.9256 | 123406.2474 | 430284.5774
| Installation | 89667.1128 | 121050.5493 | 133156.2402 | 159787.2762 | 557137.3419
| Hardware | 6738.7932 | 8583.1072 | 9336.0113 | 9787.7538 | 30457.0806
| Foundation | 37103.116 | 50088.002 | 55096.9227 | 66117.03 | 145628.5258
Non-angled deadend structure
| Steel weight (lbs.) | 28072 | 37898 | 41688 | 50025 | 162409
| Foundation size (Cu. Yd) | 25 | 34 | 38 | 45 | 168
| Material | 77370.6303 | 104451.2717 | 114896.2761 | 137876.0225 | 446673.424
| Installation | 100180.8979 | 135244.1592 | 148768.9991 | 178522.3749 | 578356.7463
| Hardware | 10631.0065 | 25749.3216 | 28008.034 | 29363.2615 | 121825.9132
| Foundation | 40847.1578 | 55143.9039 | 60657.5715 | 72789.5677 | 271794.7808
Angled deadend structure
| Steel weight (lbs.) | 33965 | 45852 | 50438 | 60525 | 162409
| Foundation size (Cu. Yd) | 30 | 41 | 45 | 54 | 168
| Material | 93610.9116 | 126375.099 | 139012.9772 | 166814.3449 | 446673.424
| Installation | 121208.4681 | 163631.3789 | 179994.5168 | 215993.6321 | 578356.7463
| Hardware | 10631.0065 | 25749.3216 | 28008.034 | 29363.2615 | 121825.9132
| Foundation | 49015.8665 | 66172.4438 | 72789.5677 | 87347.7221 | 271794.7808
Table 2.2-8: HVDC transmission – steel tower – single circuit
| Voltage class | ± 250 kV | ± 400 kV | ± 500 kV | ± 600 kV | ± 640 kV
Tangent structure
| Steel weight (lbs.) | 10227 | 15341 | 16875 | 20250 | 36036
| Foundation size (Cu. Yd) | 13 | 19 | 21 | 25 | 43
| Material | 23425.4424 | 35137.5498 | 38651.5503 | 46381.8603 | 141673.6478
| Installation | 30330.9981 | 45497.5571 | 50046.4649 | 60056.8177 | 183441.173
| Hardware | 5390.7936 | 6866.4858 | 7468.8091 | 7830.2031 | 19979.0643
| Foundation | 20525.9738 | 30788.3584 | 33867.4352 | 40641.1632 | 82576.1169
Running angle structures
| Steel weight (lbs.) | 16751 | 22614 | 24875 | 29850 | 93870
| Foundation size (Cu. Yd) | 31 | 41 | 45 | 54 | 90
| Material | 38367.9255 | 51796.5153 | 56975.4301 | 68370.7617 | 251879.6787
| Installation | 49678.6944 | 67066.7143 | 73772.4319 | 88527.7662 | 326130.8302
| Hardware | 6738.7932 | 8583.1072 | 9336.0113 | 9787.7538 | 21154.7994
| Foundation | 49356.7815 | 66631.4141 | 73294.3146 | 87953.6594 | 174626.7794
Non-angled deadend structure
| Steel weight (lbs.) | 19318 | 26080 | 28688 | 34425 | 113687
| Foundation size (Cu. Yd) | 40 | 55 | 60 | 72 | 176
| Material | 44247.9215 | 59734.3257 | 65708.8633 | 78850.1448 | 305046.4331
| Installation | 57292.7097 | 77345.2111 | 85080.0502 | 102096.0602 | 394977.045
| Hardware | 10631.0065 | 25749.3216 | 28008.034 | 29363.2615 | 103893.5435
| Foundation | 65355.6933 | 88229.5235 | 97052.3553 | 116462.8264 | 338774.3378
Angled deadend structure
| Steel weight (lbs.) | 25000 | 33750 | 37125 | 44550 | 113687
| Foundation size (Cu. Yd) | 74 | 100 | 110 | 132 | 176
| Material | 57262.7383 | 77304.3284 | 85034.6384 | 102041.075 | 305046.4331
| Installation | 74143.382 | 100093.9896 | 110103.2826 | 132123.9391 | 394977.045
| Hardware | 10631.0065 | 25749.3216 | 28008.034 | 29363.2615 | 103893.5435
| Foundation | 119817.7673 | 161753.9256 | 177929.9205 | 213515.1818 | 338774.3378
Table 2.2-9: Additional structure installation costs per acre
| Voltage class | 69 kV – 765 kV
| Forested clearing cost | 5485.8217
| Wetland matting and construction difficulties | 64027.0434
| Wetland mitigation credits | 51360.688
| Mountainous terrain | 7131.7802
Table 2.2-10: Transmission line removal/retirement ($/mile)
| Voltage class | 69 kV | 115 kV | 138 kV | 161 kV | 230 kV | 345 kV | 500 kV
| Single circuit | 228431.1163 | 265835.394 | 277821.6279 | 293256.7651 | 327212.1395 | 350803.939 | N/A
| Double circuit | 370428.8372 | 425993.1628 | N/A | N/A | N/A | N/A | N/A
Table 2.2-11: Conductor costs (<1,000 kcmil) (per 1,000 feet)
| Conductor | Material cost |  | Installation cost | Accessories cost
|  | ACSR | ACSS
| 266.8 kcmil “Waxwing” | 691.1347 | 673.1832 | 1600.2051 | 298.7651
| 266.8 kcmil “Partridge” | 833.4649 | 861.6745 | 1984.6912 | 298.7651
| 336.4 kcmil “Merlin” | 737.2959 | 821.9246 | 1819.7554 | 298.7651
| 336.4 kcmil “Linnet” | 848.8519 | 983.4886 | 2137.6118 | 298.7651
| 336.4 kcmil “Oriole” | 1059.1415 | 1091.1979 | 2515.5442 | 298.7651
| 397.5 kcmil “Chickadee” | 909.1179 | 956.5612 | 2182.3957 | 298.7651
| 397.5 kcmil “Ibis” | 1092.4801 | 1165.5686 | 2638.973 | 298.7651
| 397.5 kcmil “Lark” | 1078.3753 | 1293.794 | 2763.4941 | 298.7651
| 477 kcmil “Pelican” | 1065.5528 | 1171.9799 | 2613.8504 | 298.7651
| 477 kcmil “Flicker” | 1023.2384 | 1225.8345 | 2622.5887 | 298.7651
| 477 kcmil “Hawk” | 1273.2779 | 1360.4711 | 3079.166 | 298.7651
| 477 kcmil “Hen” | 1418.1726 | 1455.3579 | 3363.1614 | 298.7651
| 556.5 kcmil “Osprey” | 1279.6892 | 1293.794 | 3012.5363 | 298.7651
| 556.5 kcmil “Parakeet” | 1501.519 | 1495.1078 | 3511.7129 | 298.7651
| 556.5 kcmil “Dove” | 1419.4548 | 1563.0672 | 3484.4056 | 298.7651
| 636 kcmil “Kingbird” | 1236.0925 | 1455.3579 | 3138.1496 | 298.7651
| 636 kcmil “Rook” | 1401.5033 | 1683.5991 | 3594.7269 | 298.7651
| 636 kcmil “Grosbeak” | 1605.3816 | 1751.5585 | 3923.5063 | 298.7651
| 666.6 kcmil “Flamingo” | 1655.3895 | 1940.0498 | 4145.2412 | 298.7651
| 795 kcmil “Coot” | 1638.7202 | 1818.2357 | 4037.1044 | 298.7651
| 795 kcmil “Tern” | 1548.9624 | 1845.163 | 3957.3673 | 298.7651
| 795 kcmil “Cuckoo” | 1724.6312 | 2074.6864 | 4427.052 | 298.7651
| 795 kcmil “Condor” | 1791.3084 | 2074.6864 | 4510.0661 | 298.7651
| 795 kcmil “Drake” | 1940.0498 | 1951.5901 | 4558.1268 | 298.7651
| 900 kcmil “Canary” | 2196.5005 | 2141.3636 | 5084.6107 | 298.7651
| 954 kcmil “Rail” | 2046.4769 | 2082.38 | 4834.4763 | 298.7651
| 954 kcmil “Cardinal” | 2241.3794 | 2309.3389 | 5326.0068 | 298.7651
2.2-12: Conductor costs (>1,000 kcmil) (per 1,000 feet)
| Conductor | Material cost |  | Installation cost | Accessories cost
|  | ACSR | ACSS
| 1,033.5 kcmil “Ortolan” | 2243.9439 | 2774.7969 | 5845.9369 | 298.7651
| 1,033.5 kcmil “Curlew” | 2474.7496 | 2343.9597 | 5652.6016 | 298.7651
| 1,113 kcmil “Bluejay” | 2384.9918 | 2977.393 | 6241.346 | 298.7651
| 1,192.5 kcmil “Bunting” | 2223.4279 | 2492.7011 | 5506.2347 | 298.7651
| 1,272 kcmil “Bittern” | 2576.0476 | 2667.0876 | 6135.3938 | 298.7651
| 1,272 kcmil “Pheasant” | 2815.8291 | 3083.8201 | 6892.3509 | 298.7651
| 1,351.5 kcmil “Dipper” | 2786.3372 | 3381.3029 | 7185.0847 | 298.7651
| 1,351.5 kcmil “Martin” | 3453.1091 | 3004.3203 | 7591.4166 | 298.7651
| 1,431 kcmil “Bobolink” | 3158.1908 | 3515.9396 | 7794.5826 | 298.7651
| 1,590 kcmil “Lapwing” | 3256.9243 | 3449.2624 | 7842.6434 | 298.7651
| 1,590 kcmil “Falcon” | 3844.1965 | 3848.0433 | 9010.3015 | 298.7651
| 1,780 kcmil “Chukar” | 4189.1227 | 4486.6056 | 10143.0064 | 298.7651
| 2,156 kcmil “Bluebird” | 4934.1121 | 5482.9167 | 12167.0201 | 298.7651
| 2,167 kcmil “Kiwi” | 4468.654 | 6534.3647 | 12754.6722 | 298.7651
| 2,312 kcmil “Thrasher” | 5118.7566 | 5859.8993 | 12812.5636 | 298.7651
| 2,515 kcmil “Joree” | 5440.6023 | 6143.2773 | 13523.6445 | 298.7651
Table 2.2-13: ACCC conductor costs and round wire comparisons (per 1,000 feet)
| ACCC conductor size | Comparable ACSR/ACSS round wire conductor | Maximum amperage | Material cost | Installation cost | Accessories cost
| 821 kcmil | 795 kcmil “Drake” | 1468 | 4103.9999 | 4351.5987 | 298.7651
| 1,026 kcmil |  | 1708 | 5497.2029 | 4351.5987 | 298.7651
| 1,011 kcmil | 954 kcmil “Cardinal” | 1681 | 5054.3938 | 5602.7985 | 298.7651
| 1,222 kcmil |  | 1902 | 5605.1999 | 5602.7985 | 298.7651
| 1,300 kcmil | 1,272 kcmil “Bittern” | 1975 | 5432.4021 | 5786.7934 | 298.7651
| 1,582 kcmil |  | 2228 | 6685.1952 | 5786.7934 | 298.7651
| 2,242 kcmil | 2,156 kcmil “Bluebird” | 2785 | 9077.4052 | 13275.5987 | 298.7651
| 2,741 kcmil |  | 3130 | 10670.4021 | 13275.5987 | 298.7651
Table 2.2-14: OPGW and shieldwire costs (per 1,000 feet)
| Wire type | Material cost | Installation cost
| Shieldwire | 673.0268 | 1722.0887
| OPGW | 3044.8833 | 7781.3685
Table 2.3-1: Site work unit costs (per acre)
| Voltage class | 69 kV – 765 kV
| Level ground with light vegetation | 419680.8145
| Forested land | 5485.8217
| Wetland matting and construction difficulties | 64027.0434
| Wetland mitigation credits | 51360.688
Table 2.3-2: Circuit breaker unit costs
| Voltage class | 69 kV | 115 kV | 138 kV | 161 kV | 230 kV | 345 kV | 500 kV | 765 kV
| Foundation size (Cu. Yd) | 3.6 | 4.5 | 5.3 | 6.7 | 8 | 8.8 | 19.8 | 39.6
| Material cost | 51290.1467 | 64112.6834 | 67318.943 | 70523.9517 | 121814.0984 | 403269.4038 | 530853.0182 | 1547910.3565
| Installation cost | 9261.3233 | 9878.1023 | 10496.086 | 11112.8651 | 12347.6279 | 18521.4419 | 24695.2558 | 74529.0774
| Jumpers, conduit, wiring, grounding | 9878.1023 | 11112.8651 | 12347.6279 | 14817.1535 | 18521.4419 | 24695.2558 | 30869.0698 | 89435.3747
| Foundation cost | 5824.4664 | 7280.8842 | 8574.6747 | 10839.4103 | 12942.7233 | 14236.5138 | 32032.7584 | 64065.5168
Table 2.3-3: Disconnect switch (3-phase) unit costs
| Voltage class | 69 kV | 115 kV | 138 kV | 161 kV | 230 kV | 345 kV | 500 kV | 765 kV
| Foundation size (Cu. Yd) | 3.4 | 4.2 | 5.2 | 6.5 | 7.8 | 8 | 18 | 27
| Steel stand weight (pounds) | 1500 | 1750 | 2000 | 2500 | 3500 | 4000 | 5000 | 7500
| Material cost | 12822.5367 | 16028.7963 | 19233.805 | 22440.0647 | 25645.0733 | 44878.8784 | 64112.6834 | 192338.0501
| Installation cost | 7408.5767 | 8643.3395 | 9878.1023 | 11112.8651 | 12347.6279 | 18521.4419 | 24695.2558 | 74529.0774
| Jumpers, and grounding | 4939.0512 | 5557.0349 | 6173.814 | 7408.5767 | 9261.3233 | 12347.6279 | 15435.1372 | 44717.6874
| Steel stand material cost | 4203.2901 | 4903.8384 | 5604.3868 | 7005.4834 | 9807.6768 | 11208.7735 | 14010.9669 | 21016.4503
| Steel stand installation cost | 4654.7546 | 5430.547 | 6206.3394 | 7757.9243 | 10861.094 | 12456.0461 | 15515.8485 | 23273.7728
| Foundation cost | 5500.4165 | 6795.4116 | 8413.252 | 10516.565 | 12618.6734 | 12942.7233 | 29121.1275 | 43681.6913
Table 2.3-4: Bus support, bus, and fittings (3-phase) unit costs
| Voltage class | 69 kV | 115 kV | 138 kV | 161 kV | 230 kV | 345 kV | 500 kV | 765 kV
| Foundation size (Cu. Yd) | 3.1 | 3.9 | 4.8 | 6 | 7.2 | 9.6 | 14.4 | 21.6
| Steel stand weight (pounds) | 1000 | 1250 | 1500 | 1750 | 2000 | 3000 | 4500 | 6750
| Material cost | 7373.2713 | 9232.2264 | 10643.3309 | 11187.5069 | 11732.9338 | 13880.8651 | 15996.2709 | 23995.0318
| Installation cost | 8520.4656 | 10668.3505 | 12298.2374 | 12928.2676 | 13558.2978 | 16039.8698 | 18484.0978 | 27726.1467
| Steel stand material cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Steel stand installation cost | 2802.1934 | 3502.7417 | 4203.2901 | 4903.8384 | 5604.3868 | 8406.5801 | 12609.8702 | 18914.8053
| Foundation cost | 3103.1697 | 3878.9621 | 4654.7546 | 5430.547 | 6206.3394 | 9309.5091 | 13964.2637 | 20946.3955
Table 2.3-5: Voltage transformer (set of 3) unit costs
| Voltage class | 69 kV | 115 kV | 138 kV | 161 kV | 230 kV | 345 kV | 500 kV | 765 kV
| Foundation size (Cu. Yd) | 1.8 | 2.3 | 2.7 | 3.4 | 4 | 8 | 12.1 | 18.15
| Steel stand weight (pounds) | 1250 | 1350 | 1425 | 1500 | 1750 | 2000 | 2500 | 3750
| Material cost | 25645.0733 | 28851.333 | 32056.3417 | 35262.6013 | 44878.8784 | 53854.654 | 102580.2934 | 153870.4401
| Installation cost | 2469.5256 | 2777.9151 | 3087.5093 | 3395.8988 | 3704.2884 | 4939.0512 | 6173.814 | 9261.3233
| Jumpers, conduit, wiring, grounding | 7408.5767 | 8334.95 | 9261.3233 | 11112.8651 | 13890.7802 | 18521.4419 | 23148.4895 | 34722.7343
| Steel stand material cost | 3502.7417 | 3782.9611 | 3993.1256 | 4203.2901 | 4903.8384 | 5604.3868 | 7005.4834 | 10508.2252
| Steel stand installation cost | 3878.9621 | 4189.761 | 4422.2578 | 4654.7546 | 5430.547 | 6206.3394 | 7757.9243 | 11636.8864
| Foundation cost | 2911.6309 | 3721.1534 | 4368.0487 | 5500.4165 | 6471.3617 | 12942.7233 | 19575.5077 | 29363.2615
Table 2.3-6: Current transformer (set of 3) unit costs
| Voltage class | 69 kV | 115 kV | 138 kV | 161 kV | 230 kV | 345 kV | 500 kV | 765 kV
| Foundation size (Cu. Yd) | 1.8 | 2.3 | 2.7 | 3.4 | 4 | 8 | 12.1 | 18.15
| Steel stand weight (pounds) | 1250 | 1350 | 1425 | 1500 | 1750 | 2000 | 2500 | 3750
| Material cost | 79146.9512 | 98926.1832 | 134765.4859 | 148228.5239 | 161756.6129 | 269562.2463 | 471741.7496 | 707612.6245
| Installation cost | 2469.5256 | 2777.9151 | 3087.5093 | 3395.8988 | 3704.2884 | 4939.0512 | 6173.814 | 9261.3233
| Jumpers, conduit, wiring, grounding | 7408.5767 | 8334.95 | 9261.3233 | 11112.8651 | 13890.7802 | 18521.4419 | 23148.4895 | 34722.7343
| Steel stand material cost | 3502.7417 | 3782.9611 | 3993.1256 | 4203.2901 | 4903.8384 | 5604.3868 | 7005.4834 | 10508.2252
| Steel stand installation cost | 3878.9621 | 4189.761 | 4422.2578 | 4654.7546 | 5430.547 | 6206.3394 | 7757.9243 | 11636.8864
| Foundation cost | 2911.6309 | 3721.1534 | 4368.0487 | 5500.4165 | 6471.3617 | 12942.7233 | 19575.5077 | 29363.2615
Table 2.3-7: Power transformer ($/MVA)
| Voltage class | 69 kV | 115 kV | 138 kV | 161 kV | 230 kV | 345 kV | 500 kV | 765 kV
| 69 kV | 6054.7393 | 4928.858 | 5454.2693 | 5741.9945 | 6367.4841 | 7818.6199 | 10082.8923 | 14186.104
| 115 kV | 4928.858 | 6705.2484 | 5454.2693 | 5741.9945 | 6367.4841 | 7430.8164 | 9119.6383 | 11671.6358
| 138 kV | 5454.2693 | 5454.2693 | 7430.8164 | 6054.7393 | 6367.4841 | 7430.8164 | 9119.6383 | 11671.6358
| 161 kV | 5741.9945 | 5741.9945 | 6054.7393 | 8231.4431 | 6705.2484 | 7818.6199 | 9595.0104 | 11671.6358
| 230 kV | 6367.4841 | 6367.4841 | 6367.4841 | 6705.2484 | 9119.6383 | 7818.6199 | 9595.0104 | 11671.6358
| 345 kV | 7818.6199 | 7430.8164 | 7430.8164 | 7818.6199 | 7818.6199 | 11108.6952 | 10082.8923 | 12247.0862
| 500 kV | 10082.8923 | 9119.6383 | 9119.6383 | 9595.0104 | 9595.0104 | 10082.8923 | 14886.6523 | 13510.5752
| 765 kV | 14186.104 | 11671.6358 | 11671.6358 | 11671.6358 | 11671.6358 | 12247.0862 | 13510.5752 | 19953.118
Table 2.3-8: Grid supporting devices unit costs
| Voltage class | 69 kV | 115 kV | 138 kV | 161 kV | 230 kV | 345 kV | 500 kV | 765 kV
| Shunt reactor ($/MVAr) | 17406.1244 | 17406.1244 | 17406.1244 | 17406.1244 | 17406.1244 | 21545.6145 | 26790.9703 | 38697.7902
| Shunt capacitor bank ($/MVAr) | 12822.5367 | 12822.5367 | 12822.5367 | 12822.5367 | 12822.5367 | 12822.5367 | 12822.5367 | 12822.5367
| Static VAr Compensator ($/MVAr) | 123320.2773 | 123320.2773 | 123320.2773 | 123320.2773 | 123320.2773 | 123320.2773 | 123320.2773 | 123320.2773
| STATCOM ($/MVAr) | 244093.561 | 244093.561 | 244093.561 | 244093.561 | 244093.561 | 244093.561 | 244093.561 | 244093.561
| Synchronous condenser ($/MVAr) | $179,500/MVAr + $179,500/MW ($169.5/kw) (step-up to 69 kV)
| Energy storage (lithium ion) | Battery system: $250,000/MWh ($250/kwh) + Inverter: $75,800/MW ($75.8/kw) + $179,500/MW ($179.5/kw) (step-up to 69 kV)
| APFC (Advanced Power Flow Control) / SSSC (Static Series Synchronous Condensers) | $169,350/MVAr
Table 2.3-9: Control enclosure unit costs
| Voltage class | 69 kV | 115 kV | 138 kV | 161 kV | 230 kV | 345 kV | 500 kV | 765 kV
| Foundation size (Cu. Yd) | 18 | 18 | 18 | 18 | 18 | 36 | 36 | 36
| Material and installation cost | 370428.8372 | 370428.8372 | 370428.8372 | 370428.8372 | 370428.8372 | 740857.6744 | 740857.6744 | 740857.6744
| Battery and battery charger | 123476.2791 | 123476.2791 | 123476.2791 | 123476.2791 | 123476.2791 | 246952.5581 | 246952.5581 | 246952.5581
| Communication equipment | 123476.2791 | 123476.2791 | 123476.2791 | 123476.2791 | 123476.2791 | 185214.4186 | 185214.4186 | 185214.4186
| Station service power | 135823.907 | 135823.907 | 135823.907 | 135823.907 | 135823.907 | 160519.1628 | 160519.1628 | 160519.1628
| Foundation cost | 29121.1275 | 29121.1275 | 29121.1275 | 29121.1275 | 29121.1275 | 58242.255 | 58242.255 | 58242.255
Table 2.3-10: Relay panel unit costs
| Voltage class | 69 kV | 115 kV | 138 kV | 161 kV | 230 kV | 345 kV | 500 kV | 765 kV
| Material cost | 23152.1035 | 28862.1285 | 36116.5105 | 40747.1721 | 45069.4442 | 60194.9872 | 75320.5302 | 94150.3616
| Installation cost | 46304.207 | 57725.4616 | 72234.2256 | 81494.3442 | 90137.6837 | 120389.9744 | 150641.0605 | 188301.9279
Table 2.3-11: Control cable unit costs (per 1,000 feet)
| Voltage class | 69 kV | 115 kV | 138 kV | 161 kV | 230 kV | 345 kV | 500 kV | 765 kV
| Material cost | 3704.2884 | 3704.2884 | 3704.2884 | 3704.2884 | 3704.2884 | 4939.0512 | 4939.0512 | 4939.0512
| Installation cost | 6173.814 | 6173.814 | 6173.814 | 6173.814 | 6173.814 | 6173.814 | 6173.814 | 6173.814
Table 2.3-12: Conduit unit costs (per 1,000 feet)
| Voltage class | 69 kV | 115 kV | 138 kV | 161 kV | 230 kV | 345 kV | 500 kV | 765 kV
| Material cost | 3704.2884 | 3704.2884 | 3704.2884 | 3704.2884 | 3704.2884 | 3704.2884 | 3704.2884 | 3704.2884
| Installation cost | 49390.5116 | 49390.5116 | 49390.5116 | 49390.5116 | 49390.5116 | 49390.5116 | 49390.5116 | 49390.5116
Table 2.3-13: Cable trench unit costs (per foot)
| Voltage class | 69 kV | 115 kV | 138 kV | 161 kV | 230 kV | 345 kV | 500 kV | 765 kV
| Material cost per foot | 61.437 | 61.437 | 61.437 | 61.437 | 61.437 | 61.437 | 61.437 | 61.437
| Installation cost per foot | 246.9526 | 246.9526 | 246.9526 | 246.9526 | 246.9526 | 246.9526 | 246.9526 | 246.9526
Table 2.4-1: Converter station line commutated converter (LCC) – one end
| Voltage class | ± 250 kV | ± 400 kV | ± 500 kV | ± 600 kV | ± 640 kV
| Power Transfer | 500 MW | 1,500 MW | 2,000 MW | 2,400 MW | 3,000 MW
| Assumed Reactive Power Need | 167 MVAR | 500 MVAR | 667 MVAR | 800 MVAR | 1,000 MVAR
| Ground electrode line length | 20 miles | 20 miles | 20 miles | 20 miles | 20 miles
| Valve hall | 37.5294 | 137.6077 | 187.6469 | 231.4311 | 289.2889
| AC filters | 3.7529 | 13.7608 | 18.7647 | 23.1431 | 28.9289
| Reactive power | 20.6412 | 61.6733 | 82.3144 | 98.7023 | 123.3203
| AC Substation | 13.3855 | 19.6404 | 28.5223 | 28.5223 | 38.1549
| Ground electrode | 3.3776 | 4.5035 | 4.6286 | 4.8788 | 5.129
| Ground electrode line | 5.0039 | 12.5098 | 15.0118 | 18.7647 | 20.2659
Table 2.4-2: Converter station voltage source converter (VSC) – one end
| Voltage class | ± 250 kV | ± 400 kV | ± 500 kV | ± 600 kV | ± 640 kV
| Power Transfer | 500 MW | 1,500 MW | 2,000 MW | 2,400 MW | 3,000 MW
| Ground electrode line length | 20 miles | 20 miles | 20 miles | 20 miles | 20 miles
| Valve hall | 90.0705 | 287.7252 | 387.8035 | 475.3721 | 578.5779
| AC Substation | 13.3855 | 19.6404 | 28.5223 | 28.5223 | 38.1549
| Ground electrode | 3.3776 | 4.5035 | 4.6286 | 4.8788 | 5.129
| Ground electrode line | 5.0039 | 12.5098 | 15.0118 | 18.7647 | 20.2659
Table 3.1-1: Right-of-way width
AC Transmission (single and double circuit)
| Voltage class | 69 kV | 115 kV | 138 kV | 161 kV | 230 kV | 345 kV | 500 kV | 765 kV
| Feet | 80 | 90 | 95 | 100 | 125 | 175 | 200 | 225
HVDC transmission (single circuit)
| Voltage class | ± 250 kV | ± 400 kV | ± 500 kV | ± 600 kV | ± 640 kV
| Feet | 130 | 180 | 200 | 215 | 225
Table 3.1-2: Structures per mile – AC transmission - steel tower and steel pole (single circuit/double circuit)
| Voltage class | 69 kV | 115 kV | 138 kV | 161 kV | 230 kV | 345 kV | 500 kV | 765 kV
| Tangent structures | 9/9.5 | 8.5/9 | 8/8.5 | 7/7.5 | 2024-05-07 | 4.5/6 | 3.0/N/A | 3.5/N/A
| Running angle structures | 2024-01-01 | 2024-01-01 | 2024-01-01 | 2024-01-01 | 2024-01-01 | 2024-01-01 | 1/N/A | 0.25/N/A
| Non-angled deadend structures | 0.25/0.25 | 0.25/0.25 | 0.25/0.25 | 0.25/0.25 | 0.25/0.25 | 0.25/0.25 | 0.25/N/A | 0.125/N/A
| Angled deadend structures | 0.25/0.25 | 0.25/0.25 | 0.25/0.25 | 0.25/0.25 | 0.25/0.25 | 0.25/0.25 | 0.25/N/A | 0.125/N/A
Table 3.1-3: Structures per mile – AC transmission - wood pole (single circuit/double circuit)
| Voltage class | 69 kV | 115 kV | 138 kV | 161 kV | 230 kV | 345 kV | 500 kV | 765 kV
| Tangent structures | 15.5/18.5 | 13.5/16.5 | 13.5/N/A | 10.5/N/A | 7.5/N/A | N/A | N/A | N/A
| Running angle structures | 2024-01-01 | 2024-01-01 | 1/N/A | 1/N/A | 1/N/A | N/A | N/A | N/A
| Angled deadend structures | 0.5/0.5 | 0.5/0.5 | 0.5/N/A | 0.5/N/A | 0.5/N/A | N/A | N/A | N/A
Table 3.1-4: Structures per mile – HVDC transmission - steel tower and steel pole (single circuit)
| Voltage class | ± 250 kV | ± 400 kV | ± 500 kV | ± 600 kV | ± 640 kV
| Tangent structures | 4.5 | 4 | 3.5 | 3 | 3.5
| Running angle structures | 0.5 | 0.5 | 0.5 | 0.5 | 0.25
| Non-angled structures | 0.25 | 0.25 | 0.25 | 0.25 | 0.125
| Angled structures | 0.25 | 0.25 | 0.25 | 0.25 | 0.125
Table 3.1-5: Conductor selection per circuit – AC Transmission
| Voltage class | 69 kV | 115 kV | 138 kV | 161 kV | 230 kV | 345 kV | 500 kV | 765 kV
| Conductor size | 477 kcmil | 795 kcmil | 795 kcmil | 795 kcmil | 795 kcmil | 795 kcmil | 954 kcmil | 795 kcmil
| Conductor type | ACSS | ACSS | ACSS | ACSS | ACSS | ACSS | ACSR | ACSR
| Conductor quantity | 1 | 1 | 1 | 1 | 1 | 2 | 3 | 6
| Amp rating | 1175 | 1650 | 1650 | 1650 | 1650 | 3000 | 3000 | 5000
| Power rating (MVA) | 140 | 329 | 394 | 460 | 657 | 1792 | 2598 | 6625
Table 3.1-6: Conductor selection per circuit – HVDC Transmission
| Voltage class | ± 250 kV | ± 400 kV | ± 500 kV | ± 600 kV | ± 640 kV
| Conductor size | 1,590 kcmil | 1,590 kcmil | 1,590 kcmil | 1,590 kcmil | 795 kcmil
| Conductor type | ACSR | ACSR | ACSR | ACSR | ACSR
| Conductor quantity per pole | 1 | 2 | 2 | 2 | 6
| Power transfer | 500 MW | 1,500 MW | 2,000 MW | 2,400 MW | 6,000 MW
Table 3.1-7: Land and terrain type per state
| State | Land type |  |  | Terrain type
|  | (pasture, crop, and suburban/urban land |  |  | (level ground, forested, and wetland terrain sum to 100% per state)
sum to 100% per state)
|  | Pasture- land | Cropland | Suburban/ Urban | Level ground | Forested | Wetland
| Arkansas | 25% | 65% | 10% | 40% | 55% | 5%
| Illinois | 25% | 65% | 10% | 55% | 40% | 5%
| Indiana | 25% | 65% | 10% | 80% | 15% | 5%
| Iowa | 10% | 80% | 10% | 80% | 15% | 5%
| Kentucky | 25% | 65% | 10% | 65% | 25% | 10%
| Louisiana | 25% | 65% | 10% | 55% | 25% | 20%
| Michigan | 25% | 65% | 10% | 50% | 40% | 10%
| Minnesota | 10% | 80% | 10% | 70% | 25% | 5%
| Mississippi | 25% | 65% | 10% | 55% | 25% | 20%
| Missouri | 25% | 65% | 10% | 40% | 55% | 5%
| Montana | 70% | 20% | 10% | 85% | 10% | 5%
| North Dakota | 70% | 20% | 10% | 90% | 5% | 5%
| South Dakota | 50% | 40% | 10% | 90% | 5% | 5%
| Texas | 65% | 25% | 10% | 50% | 30% | 20%
| Wisconsin | 25% | 65% | 10% | 70% | 25% | 5%
Table 3.2-1: Initial assumptions – bus ratings
| Voltage class | 69 kV | 115 kV | 138 kV | 161 kV | 230 kV | 345 kV | 500 kV | 765 kV
| Amp rating | 1200 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 4000
| Power rating (MVA) | 143 | 598 | 717 | 837 | 1195 | 1793 | 2598 | 5300
Table 3.2-2: Substation upgrade – add 1 position - (ring/breaker-and-a-half/double-breaker bus)
| Scope of work | 69 kV | 115 kV | 138 kV | 161 kV | 230 kV | 345 kV | 500 kV | 765 kV
| Land required (acre) | 0.8/1.0/1.2 | 0.5/0.6/0.7 | 0.5/0.6/0.8 | 0.6/0.7/0.8 | 0.6/0.8/0.9 | 0.8/0.9/1.1 | 1.3/1.6/1.9 | 1.6/2.0/2.3
| Access road (mile) | 0/0/0 | 0/0/0 | 0/0/0 | 0/0/0 | 0/0/0 | 0/0/0 | 0/0/0 | 0/0/0
| Circuit breakers (each) | 1/2/2 | 1/2/2 | 1/2/2 | 1/2/2 | 1/2/2 | 1/2/2 | 1/2/2 | 1/2/2
| Disconnect switches (each) | 2/4/4 | 2/4/4 | 2/4/4 | 2/4/4 | 2/4/4 | 2/4/4 | 2/4/4 | 2/4/4
| Voltage transformers | 1/1/1 | 1/1/1 | 1/1/1 | 1/1/1 | 1/1/1 | 1/1/1 | 1/1/1 | 1/1/1
(set of 3)
| Bus support, bus, and fittings (3-phase) | 4/4/6 | 4/4/6 | 4/4/6 | 4/4/6 | 4/4/6 | 6/6/8 | 8/8/10 | 12/12/14
| Deadend structure | 1/1/1 | 1/1/1 | 1/1/1 | 1/1/1 | 1/1/1 | 1/1/1 | 1/1/1 | 1/1/1
| Control enclosure | 0/0/0 | 0/0/0 | 0/0/0 | 0/0/0 | 0/0/0 | 0/0/0 | 0/0/0 | 0/0/0
| Relay panel(s) | 1/2/2 | 1/2/2 | 1/2/2 | 1/2/2 | 1/2/2 | 1/2/2 | 1/2/2 | 1/2/2
| Cable trench (foot), | 50 / | 50 / | 50 / | 50 / | 60 / | 60 / | 70 / | 88 /
| conduit (10 feet), | 70 / | 70 / | 80 / | 80 / | 80 / | 90 / | 110 / | 131 /
| control cable (100 feet) | 90 | 100 | 100 | 110 | 110 | 120 | 140 | 175
Table 3.2-3: Substation upgrade – add 2 positions - (ring/breaker-and-a-half/double-breaker bus)
| Scope of work | 69 kV | 115 kV | 138 kV | 161 kV | 230 kV | 345 kV | 500 kV | 765 kV
| Land required (acre) | 0.8/1.0/1.2 | 0.9/1.1/1.4 | 1.0/1.3/1.5 | 1.1/1.4/1.7 | 1.2/1.5/1.8 | 1.5/1.9/2.3 | 2.5/3.1/3.8 | 3.1/3.9/4.7
| Access road (mile) | 0/0/0 | 0/0/0 | 0/0/0 | 0/0/0 | 0/0/0 | 0/0/0 | 0/0/0 | 0/0/0
| Circuit breakers (each) | 2/3/4 | 2/3/4 | 2/3/4 | 2/3/4 | 2/3/4 | 2/3/4 | 2/3/4 | 2/3/4
| Disconnect switches (each) | 4/6/8 | 4/6/8 | 4/6/8 | 4/6/8 | 4/6/8 | 4/6/8 | 4/6/8 | 4/6/8
| Voltage transformers | 2/2/2 | 2/2/2 | 2/2/2 | 2/2/2 | 2/2/2 | 2/2/2 | 2/2/2 | 2/2/2
(set of 3)
| Bus support, bus, and fittings (3-phase) | 8/8/12 | 8/8/12 | 8/8/12 | 8/8/12 | 8/8/12 | 12/12/16 | 16/16/20 | 20/20/24
| Deadend structure | 2/2/2 | 2/2/2 | 2/2/2 | 2/2/2 | 2/2/2 | 2/2/2 | 2/2/2 | 2/2/2
| Control enclosure | 0/0/0 | 0/0/0 | 0/0/0 | 0/0/0 | 0/0/0 | 0/0/0 | 0/0/0 | 0/0/0
| Relay panel(s) | 2/3/4 | 2/3/4 | 2/3/4 | 2/3/4 | 2/3/4 | 2/3/4 | 2/3/4 | 2/3/4
| Cable trench (foot), | 90 / | 95 / | 100 / | 105 / | 110 / | 120 / | 140 / | 175 /
| conduit (10 feet), | 135 / | 143 / | 150 / | 158 / | 165 / | 180 / | 210 / | 263 /
| control cable (100 feet) | 180 | 190 | 200 | 210 | 220 | 240 | 280 | 350
Table 3.2-4: New substation – 4 positions - (ring/breaker-and-a-half/double-breaker bus)
| Scope of work | 69 kV | 115 kV | 138 kV | 161 kV | 230 kV | 345 kV | 500 kV | 765 kV
| Land required (acre) | 3.2/4.0/4.8 | 3.6/4.6/5.4 | 4.0/5.0/6.0 | 4.4/5.6/6.6 | 4.8/6.0/7.2 | 6.0/7.6/9.0 | 10.0/12.6/15.0 | 12.4/15.6/18.8
| Access road (mile) | 1/1/1 | 1/1/1 | 1/1/1 | 1/1/1 | 1/1/1 | 1/1/1 | 1/1/1 | 1/1/1
| Circuit breakers (each) | 4/6/8 | 4/6/8 | 4/6/8 | 4/6/8 | 4/6/8 | 4/6/8 | 4/6/8 | 4/6/8
| Disconnect switches (each) | 8/12/16 | 8/12/16 | 8/12/16 | 8/12/16 | 8/12/16 | 8/12/16 | 8/12/16 | 8/12/16
| Voltage transformers | 4/6/6 | 4/6/6 | 4/6/6 | 4/6/6 | 4/6/6 | 4/6/6 | 4/6/6 | 4/6/6
(set of 3)
| Bus support, bus, and fittings (3-phase) | 12/14/16 | 12/14/16 | 12/14/16 | 12/14/16 | 12/14/16 | 14/16/20 | 20/24/32 | 28/32/48
| Deadend structure | 4/4/4 | 4/4/4 | 4/4/4 | 4/4/4 | 4/4/4 | 4/4/4 | 4/4/4 | 4/4/4
| Control enclosure | 1/1/1 | 1/1/1 | 1/1/1 | 1/1/1 | 1/1/1 | 1/1/1 | 1/1/1 | 1/1/1
| Relay panel(s) | 6/8/10 | 6/8/10 | 6/8/10 | 6/8/10 | 6/8/10 | 6/8/10 | 6/8/10 | 6/8/10
| Cable trench (foot), | 180 / | 190 / | 200 / | 210 / | 220 / | 240 / | 280 / | 350 /
| conduit (10 feet), | 270 / | 290 / | 300 / | 320 / | 330 / | 360 / | 420 / | 525 /
| control cable (100 feet) | 360 | 380 | 400 | 420 | 440 | 480 | 560 | 700
Table 3.2-5: New substation – 6 positions - (ring/breaker-and-a-half/double-breaker bus)
| Scope of work | 69 kV | 115 kV | 138 kV | 161 kV | 230 kV | 345 kV | 500 kV | 765 kV
| Land required (acre) | 4.0/5.0/6.0 | 4.6/5.6/6.8 | 5.0/6.2/7.6 | 5.6/6.8/8.2 | 6.0/7.6/9.0 | 7.6/9.4/11.2 | 12.6/15.6/18.8 | 15.6/19.6/23.4
| Access road (mile) | 1/1/1 | 1/1/1 | 1/1/1 | 1/1/1 | 1/1/1 | 1/1/1 | 1/1/1 | 1/1/1
| Circuit breakers | 6/9/12 | 6/9/12 | 6/9/12 | 6/9/12 | 6/9/12 | 6/9/12 | 6/9/12 | 6/9/12
| Disconnect switches (each) | 12/18/24 | 12/18/24 | 12/18/24 | 12/18/24 | 12/18/24 | 12/18/24 | 12/18/24 | 12/18/24
| Voltage transformers | 6/8/8 | 6/8/8 | 6/8/8 | 6/8/8 | 6/8/8 | 6/8/8 | 6/8/8 | 6/8/8
(set of 3)
| Bus support, bus, and fittings (3-phase) | 14/16/20 | 14/16/20 | 14/16/20 | 14/16/20 | 14/16/20 | 16/20/24 | 24/32/40 | 32/48/60
| Deadend structure | 6/6/6 | 6/6/6 | 6/6/6 | 6/6/6 | 6/6/6 | 6/6/6 | 6/6/6 | 6/6/6
| Control enclosure | 1/1/1 | 1/1/1 | 1/1/1 | 1/1/1 | 1/1/1 | 1/1/1 | 1/1/1 | 1/1/1
| Relay panel(s) | 8/11/14 | 8/11/14 | 8/11/14 | 8/11/14 | 8/11/14 | 8/11/14 | 8/11/14 | 8/11/14
| Cable trench (foot), | 270 / | 290 / | 300 / | 320 / | 330 / | 360 / | 420 / | 525 /
| conduit (10 feet), | 410 / | 430 / | 450 / | 470 / | 500 / | 540 / | 630 / | 788/
| control cable (100 feet) | 540 | 570 | 600 | 630 | 600 | 720 | 840 | 1050
Table 4.1-1: Exploratory cost estimate – AC transmission - new single circuit transmission line $/mile
| Location | 69 kV | 115 kV | 138 kV | 161 kV | 230 kV | 345 kV | 500 kV | 765 kV
| Arkansas | 1.8192 | 2.0216 | 2.1148 | 2.1558 | 2.2992 | 3.6677 | 4.6494 | 5.8797
| Illinois | 1.8363 | 2.0407 | 2.135 | 2.1771 | 2.3258 | 3.705 | 4.692 | 5.9276
| Indiana | 1.7614 | 1.9565 | 2.0461 | 2.0836 | 2.2089 | 3.5412 | 4.5048 | 5.7171
| Iowa | 1.8124 | 2.0139 | 2.1067 | 2.1473 | 2.2886 | 3.6528 | 4.6324 | 5.8606
| Kentucky | 1.9016 | 2.1143 | 2.2126 | 2.2588 | 2.428 | 3.848 | 4.8554 | 6.1114
| Louisiana | 2.0565 | 2.2885 | 2.3965 | 2.4524 | 2.6699 | 4.1867 | 5.2425 | 6.5469
| Michigan | 1.8804 | 2.0904 | 2.1874 | 2.2323 | 2.3948 | 3.8016 | 4.8023 | 6.0518
| Minnesota | 1.8683 | 2.0768 | 2.173 | 2.2172 | 2.3759 | 3.775 | 4.772 | 6.0176
| Mississippi | 2.0464 | 2.2772 | 2.3846 | 2.4398 | 2.6542 | 4.1647 | 5.2174 | 6.5187
| Missouri | 1.7933 | 1.9924 | 2.084 | 2.1234 | 2.2587 | 3.611 | 4.5845 | 5.8067
| Montana | 1.6704 | 1.8541 | 1.938 | 1.9698 | 2.0667 | 3.3421 | 4.2773 | 5.4611
| North Dakota | 1.7016 | 1.8892 | 1.9751 | 2.0088 | 2.1154 | 3.4104 | 4.3553 | 5.5488
| South Dakota | 1.7004 | 1.8879 | 1.9737 | 2.0073 | 2.1136 | 3.4078 | 4.3524 | 5.5456
| Texas | 1.9847 | 2.2077 | 2.3113 | 2.3627 | 2.5578 | 4.0297 | 5.0631 | 6.3451
| Wisconsin | 1.9878 | 2.21 | 2.3128 | 2.361 | 2.5373 | 4.0219 | 5.0755 | 6.3893
Includes contingency (30%) and AFUDC (7.5%)
Table 4.1-2: Exploratory cost estimate – AC transmission - new double circuit transmission line $/mile
| Location | 69 kV | 115 kV | 138 kV | 161 kV | 230 kV | 345 kV
| Arkansas | 2.5916 | 2.926 | 3.0929 | 3.1683 | 3.7203 | 6.0992
| Illinois | 2.6086 | 2.9452 | 3.1132 | 3.1896 | 3.7469 | 6.1364
| Indiana | 2.5337 | 2.8609 | 3.0243 | 3.096 | 3.6299 | 5.9727
| Iowa | 2.5848 | 2.9183 | 3.0848 | 3.1598 | 3.7096 | 6.0843
| Kentucky | 2.674 | 3.0187 | 3.1908 | 3.2713 | 3.849 | 6.2794
| Louisiana | 2.8288 | 3.1929 | 3.3747 | 3.4648 | 4.0909 | 6.6181
| Michigan | 2.6527 | 2.9948 | 3.1656 | 3.2448 | 3.8158 | 6.233
| Minnesota | 2.6406 | 2.9812 | 3.1512 | 3.2296 | 3.7969 | 6.2065
| Mississippi | 2.8188 | 3.1816 | 3.3627 | 3.4523 | 4.0753 | 6.5962
| Missouri | 2.5656 | 2.8968 | 3.0621 | 3.1358 | 3.6797 | 6.0424
| Montana | 2.4427 | 2.7586 | 2.9162 | 2.9822 | 3.4877 | 5.7736
| North Dakota | 2.4739 | 2.7937 | 2.9532 | 3.0212 | 3.5365 | 5.8419
| South Dakota | 2.4728 | 2.7923 | 2.9519 | 3.0198 | 3.5346 | 5.8393
| Texas | 2.757 | 3.1122 | 3.2894 | 3.3751 | 3.9788 | 6.4612
| Wisconsin | 2.6718 | 3.0162 | 3.1882 | 3.2685 | 3.8456 | 6.2746
Includes contingency (30%) and AFUDC (7.5%)
Table 4.1-3: Exploratory cost estimate – AC transmission - rebuild and reconductor transmission line $/mile
| Scope of Work | 69 kV | 115 kV | 138 kV | 161 kV | 230 kV | 345 kV | 500 kV | 765 kV
| Rebuild – single circuit | 1.5979 | 1.7725 | 1.8518 | 1.8788 | 1.9517 | N/A | N/A | N/A
| Rebuild – double circuit | 2.3643 | 2.6704 | N/A | N/A | N/A | N/A | N/A | N/A
| Reconductor – per circuit | 0.4067 | 0.47594 | 0.47958 | 0.48191 | 0.48191 | 0.757 | 1.0528 | 1.457
Includes contingency (30%) and AFUDC (7.5%)
Table 4.1-4: Exploratory cost estimate – HVDC transmission - new bipole transmission line $/mile
| Location | 250 kV | 400 kV | 500 kV | 600 kV | 640 kV
| Arkansas | 2.4248 | 2.8727 | 3.0174 | 3.2114 | 5.7606
| Illinois | 2.4525 | 2.911 | 3.0599 | 3.2572 | 5.8085
| Indiana | 2.3308 | 2.7426 | 2.8728 | 3.056 | 5.598
| Iowa | 2.4137 | 2.8574 | 3.0003 | 3.1931 | 5.7415
| Kentucky | 2.5587 | 3.0581 | 3.2233 | 3.4328 | 5.9924
| Louisiana | 2.8103 | 3.4065 | 3.6105 | 3.849 | 6.4279
| Michigan | 2.5242 | 3.0103 | 3.1703 | 3.3758 | 5.9327
| Minnesota | 2.5045 | 2.983 | 3.14 | 3.3432 | 5.8986
| Mississippi | 2.794 | 3.3839 | 3.5853 | 3.822 | 6.3996
| Missouri | 2.3826 | 2.8143 | 2.9525 | 3.1416 | 5.6876
| Montana | 2.1829 | 2.5378 | 2.6453 | 2.8114 | 5.342
| North Dakota | 2.2336 | 2.608 | 2.7233 | 2.8952 | 5.4298
| South Dakota | 2.2317 | 2.6054 | 2.7203 | 2.8921 | 5.4265
| Texas | 2.6937 | 3.245 | 3.4311 | 3.6561 | 6.2261
| Wisconsin | 2.674 | 3.1952 | 3.3676 | 3.5864 | 6.2646
Includes contingency (30%) and AFUDC (7.5%)
Table 4.2-1: Exploratory cost estimate – substation upgrade
| Scope of work | 69 kV | 115 kV | 138 kV | 161 kV | 230 kV | 345 kV | 500 kV | 765 kV
| Add 1 position (ring bus) | 1.3189 | 1.5282 | 1.7183 | 1.9084 | 2.2396 | 3.5581 | 5.4814 | 18.3689
| Add 1 position (breaker-and-a-half bus) | 1.8156 | 2.1146 | 2.3875 | 2.6595 | 3.1586 | 5.144 | 7.66 | 23.1721
| Add 1 position (double-breaker bus) | 2.0492 | 2.3836 | 2.6893 | 2.9899 | 3.5177 | 5.5931 | 8.2991 | 23.978
| Add 2 positions(ring bus) | 2.6285 | 3.0461 | 3.4253 | 3.8041 | 4.4651 | 7.0991 | 10.9399 | 28.074
| Add 2 positions (breaker-and-a-half bus) | 3.2765 | 3.7984 | 4.2748 | 4.7502 | 5.5937 | 8.9404 | 13.499 | 33.3523
| Add 2 positions (double-breaker bus) | 4.0891 | 4.7568 | 5.3672 | 5.9672 | 7.0213 | 11.1691 | 16.5753 | 39.2922
Includes contingency (30%) and AFUDC (7.5%)
Table 4.2-2: Exploratory cost estimate – new substation
| Scope of work | 69 kV | 115 kV | 138 kV | 161 kV | 230 kV | 345 kV | 500 kV | 765 kV
| 4 positions (ring bus) | 9.1413 | 10.163 | 11.1268 | 12.0742 | 13.5828 | 19.9234 | 28.9191 | 56.0419
| 4 positions (breaker-and-a-half bus) | 11.013 | 12.326 | 13.5638 | 14.7837 | 16.762 | 24.7744 | 36.1675 | 69.37
| 4 positions (double-breaker bus) | 12.7441 | 14.3304 | 15.8253 | 17.2963 | 19.6977 | 29.5057 | 43.4225 | 83.949
| 6 positions (ring bus) | 11.5136 | 12.8895 | 14.1764 | 15.4592 | 17.5852 | 26.0368 | 38.2844 | 73.4669
| 6 positions (breaker-and-a-half bus) | 14.0334 | 15.7828 | 17.5071 | 19.1369 | 21.8929 | 32.9448 | 48.5871 | 94.0585
| 6 positions (double-breaker bus) | 16.4948 | 18.7087 | 20.6955 | 22.7531 | 26.1068 | 39.5394 | 58.4673 | 113.254
Includes contingency (30%) and AFUDC (7.5%)
Table 4.3-1: Exploratory cost estimate – HVDC transmission converter Station (costs are or one of multiple required ends)
| Scope of work | 250 kV | 400 kV | 500 kV | 600 kV | 640 kV
| Line Commutated Converter | 128.6532 | 383.8443 | 517.8821 | 623.2663 | 776.4463
| Voltage Source Converter | 171.9223 | 498.6515 | 670.1891 | 810.9577 | 987.1107
Includes contingency (30%) and AFUDC (7.5%)

## Exploratory cost estimate
MISO
Cost Estimation Guide / Workbook for MTEP25
Exploratory Cost Estimate (2025 dollars)
This is not a Planning or Scoping level estimate
XX/XX/2025
Input cells-teal color
| Line | Amounts include overhead, 30% contingency, 7.5% AFUDC
State: | Illinois | Enter via drop down list
Line type: | A/C | Enter via drop down list
New / Rebuild / Reconductor: | New | Enter via drop down list
Circuit: | Single | Enter via drop down list
Voltage class: | 345 kV | Enter via drop down list
Line length (miles): | 100 | Enter number of miles - recommend 30% adder to the straight line distance for exploratory estimate
Total Capital Cost | 370.4987 | MTEP25 Exploratory Line Total Capital Cost includes contingency (30%) and AFUDC (7.5%)
Project Cost | 265.1155 | If Wisconsin, includes 5% environmental fee
Contingency | 79.5347 | 30%
AFUDC | 25.8488 | 7.5%
Project Implementation Cost (2025$) | 370.4989
| Substation #1 | Amounts include overhead, 30% contingency, 7.5% AFUDC
Facility: | New - 4 positions (ring bus) | Enter via drop down list
Voltage class: | 230 kV | Enter via drop down list
Total Capital Cost | 13.5828 | MTEP25 Exploratory Line Total Capital Cost includes contingency (30%) and AFUDC (7.5%)
Project Cost | 9.7194
Contingency | 2.9158 | 30%
AFUDC | 0.94764 | 7.5%
Total Capital Cost | 13.5828
| Substation #2 | Amounts include overhead, 30% contingency, 7.5% AFUDC
Facility: | Upgrade - Add one position (breaker-and-a-half bus) | Enter via drop down list
Voltage class: | 161 kV | Enter via drop down list
Total Capital Cost | 2.6595 | MTEP25 Exploratory Line Total Capital Cost includes contingency (30%) and AFUDC (7.5%)
Project Cost | 1.903
Contingency | 0.57091 | 30%
AFUDC | 0.18555 | 7.5%
Total Capital Cost | 2.6595
Add Transformer (breakers included)
Primary voltage class: | 345 kV | Enter via drop down list
Secondary voltage class: | 161 kV | Enter via drop down list
Transformer MVA: | 400 | Enter MVA top rating (only type the number, the cell format will add the MVA)
Total Capital Cost | 12.6112 | MTEP25 Exploratory Line Total Capital Cost includes contingency (30%) and AFUDC (7.5%)
Project Cost | 9.0241
Contingency | 2.7072 | 30%
AFUDC | 0.87985 | 7.5%
Total Capital Cost | 12.6112
Grand Total
Project Cost from above | 285762039.8383
Market uncertainty cost adder % | 28576203.9838 | 10% | Market uncertainty cost adder %
Additional Cost not included above | 2000
Additional Cost not included above | 3000
Additional Cost not included above | 4000
Project Cost Subtotal | 314347243.8221
Contingency | 94304173.1466 | 30%
AFUDC | 30648856.2727 | 7.5%
Total Capital Cost | 439300273.2415
| 4.8077 |  | 4807669.39 | 12019.1735
400
| 5.144 |  |  | 4807669.39
2.6595

## Line Exploratory example
Illinois
|  |  |  | Line Type: | A/C
|  |  |  | Voltage class: | 345 kV
|  |  |  | Facility type (Circuit): | Single
|  |  |  | Structure type: | Steel Pole
|  |  |  | Line length (miles): | 1
|  |  |  | Conductor: | 795 "Drake"
|  |  |  | Conductor type: | ACSS
|  |  |  | Conductors per phase: | 2
|  |  |  | Shieldwire quantity: | 1
|  |  |  | OPGW quantity: | 1
Right-of-Way, land acquisition, and regulatory and permitting
| ROW width in feet | Allocation % | Unit / Acres | Unit Cost
Pasture land | 175 | 25% | 5.303 | 22032.8605 | 116840.9267
Crop land | 175 | 65% | 13.7879 | 30290.4605 | 417641.1973
Suburban/urban land | 175 | 10% | 2.1212 | 38548.0605 | 81768.6131
616250.7371
Structure material |  |  |  |  | Cost per Pound
Structures | Units per Mile | Number of Structures | Steel Weights (lbs.) | Total Steel Pounds | 2.7503
Tangent | 4.5 | 4.5 | 22300 | 100350 | 275992.6963
Running angle | 1 | 1 | 37900 | 37900 | 104236.4045
Non-angled deadend | 0.25 | 0.25 | 42400 | 10600 | 29153.1896
Angled deadend | 0.25 | 0.25 | 48100 | 12025 | 33072.3684
442454.6589
Structure foundation |  |  |  |  | Cost per Cu. Yd.
Structures | Foundation size (Cu. Yd) | Number of Foundations | Total Cubic Yards |  | 1617.8404
Tangent | 21 | 4.5 | 94.5 |  | 152885.9194
Running angle | 30 | 1 | 30 |  | 48535.2125
Non-angled deadend | 33.5 | 0.25 | 8.375 |  | 13549.4135
Angled deadend | 41.5 | 0.25 | 10.375 |  | 16785.0943
231755.6398
Structure Hardware / Insulators / Grounding - "Hardware" data
Structures |  | Number of Structures | Cost per Unit
Tangent |  | 4.5 | 11091.1815 |  | 49910.3166
Running angle |  | 1 | 11091.1815 |  | 11091.1815
Non-angled deadend |  | 0.25 | 39865.3708 |  | 9966.3427
Angled deadend |  | 0.25 | 39865.3708 |  | 9966.3427
|  |  |  | Total Structure and conductor accessories | 80934.1835
Structure construction labor "Installation data"
Structures | Unit of Measure | Number of Units | Cost per Unit
Tangent | Each | 4.5 | 79412.9928 |  | 357358.4676
Running angle | Each | 1 | 134966.4766 |  | 134966.4766
Non-angled deadend | Each | 0.25 | 150991.52 |  | 37747.88
Angled deadend | Each | 0.25 | 171289.9083 |  | 42822.4771
6
Forested | Right-of-way width in feet | 175
Forested | Percentage | 40%
Project length | Miles | 1
Forested clearing | ACRE | 8.4848 | 5485.8217 |  | 46546.3662
Wetland | Right-of-way width in feet | 175
Wetland | Wetland percentage | 5%
Project length | Miles | 1
Wetland matting & construction | ACRE | 1.0606 | 64027.0434 |  | 67907.4703
Wetland mitigation credits | ACRE | 1.0606 | 51360.688 |  | 54473.457
Mountainous | ACRE |  | 7131.7802 |  | 0
741822.5947
Conductor "Materials" data plus "Accessories" data
|  |  | Conductor Material | $ per Phase
|  |  | Conductor (Type / Phase) | ACSS 795 "Drake" | 1951.5901
|  |  | Conductors per phase: |  | 2
|  |  | Facility type (Circuit): | Single | 1
|  |  | Line length (miles): |  | 1
|  |  |  | Wastage, Sag, Clipping | 1.04
|  |  |  | Feet to Mile calculation | 5.28
|  |  |  | Conductor phases | 3
|  |  |  | Sub-total | 64299.4287
|  |  | Conductor Accessories | $ per Phase
|  |  | Conductor (Type / Phase) | ACSS 795 "Drake" | 298.7651
|  |  | Conductors per phase: |  | 2
|  |  | Facility type (Circuit): | Single | 1
|  |  | Line length (miles): |  | 1
|  |  |  | Wastage, Sag, Clipping | 1.04
|  |  |  | Feet to Mile calculation | 5.28
|  |  |  | Conductor phases | 3
|  |  |  | Sub-total | 9843.4736
|  |  |  | Total Conductor materials and accessories | 74142.9024
Conductor Construction Labor "Installation data"
|  |  | Conductor Material | $ per Phase
|  |  | Conductor (Type / Phase) | ACSS 795 "Drake" | 4558.1268
|  |  | Conductors per phase: |  | 2
|  |  | Facility type (Circuit): | Single | 1
|  |  | Line length (miles): |  | 1
|  |  |  | Sag, clip, waste factor | 1.04
|  |  |  | Mile to feet | 5.28
|  |  |  | 3 Phase | 3
150177.5167
OPGW and /or Shieldwire "Material data"
|  | Conductor Material | Quantity | $ per 1,000 feet
|  | Shieldwire | 1 | 673.0268 | 673.0268
|  | OPGW | 1 | 3044.8833 | 3044.8833
|  | Total cost per 1,000 feet |  |  | 3717.9101
|  |  |  | Line length (miles): | 1
|  |  |  | Sag, clip, waste factor | 1.04
|  |  |  | Mile to feet | 5.28
20415.7882
OPGW and /or Shieldwire "Installation data"
|  | Conductor Material | Quantity | $ per 1,000 feet
|  | Shieldwire | 1 | 1722.0887 | 1722.0887
|  | OPGW | 1 | 7781.3685 | 7781.3685
|  | Total cost per 1,000 feet |  |  | 9503.4572
|  |  |  | Line length (miles): | 1
|  |  |  | Sag, clip, waste factor | 1.04
|  |  |  | Mile to feet | 5.28
52185.3843
|  |  | Project management | 5.5% | 132557.6673
|  |  | Engineering, environmental studies, and testing and commissioning | 3% | 72304.1822
|  |  | Administrative & General overhead (A&G) | 1.5% | 36152.0911
|  |  | Right-of-Way, land acquisition, and regulatory and permitting |  | 616250.7371
|  |  | Structure material |  | 442454.6589
|  |  | Structure foundations |  | 231755.6398
|  |  | Structure and conductor accessories |  | 80934.1835
|  |  | Structure construction labor |  | 741822.5947
|  |  | Conductor material |  | 74142.9024
|  |  | Conductor construction labor |  | 150177.5167
|  |  | OPGW, and/or shieldwire material |  | 20415.7882
|  |  | OPGW and/or shieldwire construction labor |  | 52185.3843
|  |  | Sub-total Project Costs |  | 2651153.3462
|  |  | Contingency: | 30% | 795346.0038
|  |  | AFUDC: | 7.5% | 258487.4513
|  |  | Sub-total Project Implementation |  | 1053833.4551
|  |  | Total Capital Cost |  | 3704986.8013
3.705

## Substation Explor. example
|  |  |  | State: | Illinois
|  |  |  | Facility type and scope of work: | New site - 4 positions (double-breaker bus)
|  |  |  | Voltage class: | 345 kV
|  |  |  | Land Type: | Suburban/urban land
|  |  |  | Terrain Type: | Wetland
Electrical equipment material - Power transformer (MVA)
|  |  |  | Electrical equipment material - Bus or Transformer secondary voltage | 345 kV
Electrical equipment material - (MVAr) type
Electrical equipment material - (MVAr) size
|  |  | acres | Land required | 9
|  |  | miles | Access road | 1
|  |  | each | Circuit breaker | 8
|  |  | each | Disconnect switch | 16
|  |  | set of 3 | Voltage transformer | 6
|  |  | 3-phase | Bus support, bus, and fittings | 20
|  |  | each | Deadend structure | 4
|  |  | each | Control enclosure | 1
|  |  | each | Relay panel | 10
|  |  | feet | Control cable | 48000
|  |  | feet | Conduit | 4800
|  |  | per foot | Cable trench | 480
Land acquisition, and regulatory and permitting
State | Land & Terrain Type | Acres | Cost per acre
Illinois | Suburban/urban land | 9 | 38548.0605 |  | 346932.5442
346932.5442
Site work
| Terrain Type | Acres | Cost per acre
Site work | Applies to all types | 9 | 419680.8145 |  | 3777127.3301
| Wetland | 9 | 64027.0434 |  | 576243.3907
| Wetland mitigation credits | 9 | 51360.688 |  | 462246.1921
4815616.9129
Access Road
Access road |  |  | Unit Cost per mile | 648250.4651 | 648250.4651
Steel support structure material
Cost per Pound
Structures | Units | Number of units | Steel stand weight | Total Steel Pounds | 2.7503
Disconnect switch | each | 16 | 4000 | 64000 | 176019.2582
Voltage transformer | set of 3 | 6 | 2000 | 12000 | 33003.6109
Bus support, bus, and fittings | 3-phase | 20 | 3000 | 60000 | 165018.0546
Deadend structure | each | 4 | 48100 | 192400 | 529157.8951
|  |  |  | Total Structure Material | 903198.8188
Steel support structure installation
Structures | Units | Number of units | Steel stand installation
Disconnect switch | each | 16 | 12456.0461 |  | 199296.7376
Voltage transformer | set of 3 | 6 | 6206.3394 |  | 37238.0365
Bus support, bus, and fittings | 3-phase | 20 | 9309.5091 |  | 186190.1824
Deadend structure | each | 4 | 171289.9083 |  | 685159.633
1107884.5895
Substation foundations
Cost per Cu. Yd.
Structures | Units | Number of Structures | Foundation size Cu. Yd. | Total Cubic Yards | 1617.8404
Circuit breaker | Circuit breaker | 8 | 8.8 | 70.4 | 113895.9654
Disconnect switch | Disconnect switch | 16 | 8 | 128 | 207083.5734
Voltage transformer | Voltage transformer | 6 | 8 | 48 | 77656.34
Bus support, bus, and fittings | Bus support, bus, and fittings | 20 | 9.6 | 192 | 310625.3601
Deadend structure | Deadend structure | 4 | 41.5 | 166 | 268561.5093
Control Enclosure | Control enclosure | 1 | 36 | 36 | 58242.255
1036065.0033
Electrical equipment material
Structures | Unit of Measure | Number of Units | Material | Jumpers, conduit, wiring, grounding
Circuit breaker | each | 8 | 403269.4038 | 24695.2558 | 3423717.2771
Disconnect switch | each | 16 | 44878.8784 | 12347.6279 | 915624.1001
Voltage transformer | set of 3 | 6 | 53854.654 | 18521.4419 | 434256.5753
Bus support, bus, and fittings | 3-phase | 20 | 13880.8651 | 0 | 277617.3013
Power transformer | MVA | 0 | 0 |  | 0
MVAr Equipment | MVAr | 0 | 0 |  | 0
5051215.2538
Electrical equipment installation
Structures | Unit of Measure | Number of Units | Installation
Circuit breaker | each | 8 | 18521.4419 |  | 148171.5349
Disconnect switch | each | 16 | 18521.4419 |  | 296343.0698
Voltage transformer | set of 3 | 6 | 4939.0512 |  | 29634.307
Bus support, bus, and fittings | 3-phase | 20 | 16039.8698 |  | 320797.3962
Hardware/Insulators/Grounding |  | 4 | 39865.3708 |  | 159461.483
954407.7909
Control enclosure - not including communication equipment
Structures |  | Number of Units | All except comm. equip.
Control enclosure | each | 1 | 1391786.0689 |  | 1391786.0689
Relay panels
Structures |  | Number of Units | Material | Installation
Relay panel | each | 10 | 60194.9872 | 120389.9744 | 1805849.6161
Communication system
Structures |  | Number of Units | Communication equipment
Control enclosure | each | 1 | 185214.4186 |  | 185214.4186
Control cable, conduit, and cable trench
Structures |  | Number of Units | Material | Installation
Control cable | feet | 48000 | 4.9391 | 6.1738 | 533417.5256
Conduit | feet | 4800 | 3.7043 | 49.3905 | 254855.04
Cable trench | per foot | 480 | 61.437 | 246.9526 | 148026.9773
936299.5428
|  |  | Project management | 5.5% | 1055049.6564
|  |  | Engineering, environmental studies, and testing and commissioning | 3% | 575481.6307
|  |  | Administrative & General overhead (A&G) | 1.5% | 287740.8154
|  |  | Land acquisition, and regulatory and permitting |  | 346932.5442
|  |  | Site work |  | 4815616.9129
|  |  | Access roads |  | 648250.4651
|  |  | Steel support structure material |  | 903198.8188
|  |  | Steel support structure construction labor |  | 1107884.5895
|  |  | Substations foundations |  | 1036065.0033
|  |  | Electrical equipment material |  | 5051215.2538
|  |  | Electrical equipment construction labor |  | 954407.7909
|  |  | Control enclosure |  | 1391786.0689
|  |  | Relay panels |  | 1805849.6161
|  |  | Communication system |  | 185214.4186
|  |  | Control cable, conduit, and cable trench |  | 936299.5428
|  |  | Sub-total Project Costs |  | 21100993.1273
|  |  | Contingency: | 30% | 6330297.9382
|  |  | AFUDC: | 7.5% | 2057346.8299
|  |  | Sub-total Project Implementation |  | 8387644.7681
|  |  | Total Capital Cost |  | 29488637.8954
29.4886

## Exploratory cost data (hidden)
State | Line Type | Type | Circuit | Concatenate | N/A | 69 kV | 115 kV | 138 kV | 161 kV | 230 kV | 345 kV | 500 kV | 765 kV | ± 250 kV | ± 400 kV | ± 500 kV | ± 600 kV | ± 640 kV
Arkansas | A/C | New | Single | ArkansasA/CNewSingle |  | 1.8192 | 2.0216 | 2.1148 | 2.1558 | 2.2992 | 3.6677 | 4.6494 | 5.8797
Illinois | A/C | New | Single | IllinoisA/CNewSingle |  | 1.8363 | 2.0407 | 2.135 | 2.1771 | 2.3258 | 3.705 | 4.692 | 5.9276
Indiana | A/C | New | Single | IndianaA/CNewSingle |  | 1.7614 | 1.9565 | 2.0461 | 2.0836 | 2.2089 | 3.5412 | 4.5048 | 5.7171
Iowa | A/C | New | Single | IowaA/CNewSingle |  | 1.8124 | 2.0139 | 2.1067 | 2.1473 | 2.2886 | 3.6528 | 4.6324 | 5.8606
Kentucky | A/C | New | Single | KentuckyA/CNewSingle |  | 1.9016 | 2.1143 | 2.2126 | 2.2588 | 2.428 | 3.848 | 4.8554 | 6.1114
Louisiana | A/C | New | Single | LouisianaA/CNewSingle |  | 2.0565 | 2.2885 | 2.3965 | 2.4524 | 2.6699 | 4.1867 | 5.2425 | 6.5469
Michigan | A/C | New | Single | MichiganA/CNewSingle |  | 1.8804 | 2.0904 | 2.1874 | 2.2323 | 2.3948 | 3.8016 | 4.8023 | 6.0518
Minnesota | A/C | New | Single | MinnesotaA/CNewSingle |  | 1.8683 | 2.0768 | 2.173 | 2.2172 | 2.3759 | 3.775 | 4.772 | 6.0176
Mississippi | A/C | New | Single | MississippiA/CNewSingle |  | 2.0464 | 2.2772 | 2.3846 | 2.4398 | 2.6542 | 4.1647 | 5.2174 | 6.5187
Missouri | A/C | New | Single | MissouriA/CNewSingle |  | 1.7933 | 1.9924 | 2.084 | 2.1234 | 2.2587 | 3.611 | 4.5845 | 5.8067
Montana | A/C | New | Single | MontanaA/CNewSingle |  | 1.6704 | 1.8541 | 1.938 | 1.9698 | 2.0667 | 3.3421 | 4.2773 | 5.4611
North Dakota | A/C | New | Single | North DakotaA/CNewSingle |  | 1.7016 | 1.8892 | 1.9751 | 2.0088 | 2.1154 | 3.4104 | 4.3553 | 5.5488
South Dakota | A/C | New | Single | South DakotaA/CNewSingle |  | 1.7004 | 1.8879 | 1.9737 | 2.0073 | 2.1136 | 3.4078 | 4.3524 | 5.5456
Texas | A/C | New | Single | TexasA/CNewSingle |  | 1.9847 | 2.2077 | 2.3113 | 2.3627 | 2.5578 | 4.0297 | 5.0631 | 6.3451
Wisconsin | A/C | New | Single | WisconsinA/CNewSingle |  | 1.9878 | 2.21 | 2.3128 | 2.361 | 2.5373 | 4.0219 | 5.0755 | 6.3893
Arkansas | A/C | New | Double | ArkansasA/CNewDouble |  | 2.5916 | 2.926 | 3.0929 | 3.1683 | 3.7203 | 6.0992 | N/A | N/A
Illinois | A/C | New | Double | IllinoisA/CNewDouble |  | 2.6086 | 2.9452 | 3.1132 | 3.1896 | 3.7469 | 6.1364 | N/A | N/A
Indiana | A/C | New | Double | IndianaA/CNewDouble |  | 2.5337 | 2.8609 | 3.0243 | 3.096 | 3.6299 | 5.9727 | N/A | N/A
Iowa | A/C | New | Double | IowaA/CNewDouble |  | 2.5848 | 2.9183 | 3.0848 | 3.1598 | 3.7096 | 6.0843 | N/A | N/A
Kentucky | A/C | New | Double | KentuckyA/CNewDouble |  | 2.674 | 3.0187 | 3.1908 | 3.2713 | 3.849 | 6.2794 | N/A | N/A
Louisiana | A/C | New | Double | LouisianaA/CNewDouble |  | 2.8288 | 3.1929 | 3.3747 | 3.4648 | 4.0909 | 6.6181 | N/A | N/A
Michigan | A/C | New | Double | MichiganA/CNewDouble |  | 2.6527 | 2.9948 | 3.1656 | 3.2448 | 3.8158 | 6.233 | N/A | N/A
Minnesota | A/C | New | Double | MinnesotaA/CNewDouble |  | 2.6406 | 2.9812 | 3.1512 | 3.2296 | 3.7969 | 6.2065 | N/A | N/A
Mississippi | A/C | New | Double | MississippiA/CNewDouble |  | 2.8188 | 3.1816 | 3.3627 | 3.4523 | 4.0753 | 6.5962 | N/A | N/A
Missouri | A/C | New | Double | MissouriA/CNewDouble |  | 2.5656 | 2.8968 | 3.0621 | 3.1358 | 3.6797 | 6.0424 | N/A | N/A
Montana | A/C | New | Double | MontanaA/CNewDouble |  | 2.4427 | 2.7586 | 2.9162 | 2.9822 | 3.4877 | 5.7736 | N/A | N/A
North Dakota | A/C | New | Double | North DakotaA/CNewDouble |  | 2.4739 | 2.7937 | 2.9532 | 3.0212 | 3.5365 | 5.8419 | N/A | N/A
South Dakota | A/C | New | Double | South DakotaA/CNewDouble |  | 2.4728 | 2.7923 | 2.9519 | 3.0198 | 3.5346 | 5.8393 | N/A | N/A
Texas | A/C | New | Double | TexasA/CNewDouble |  | 2.757 | 3.1122 | 3.2894 | 3.3751 | 3.9788 | 6.4612 | N/A | N/A
Wisconsin | A/C | New | Double | WisconsinA/CNewDouble |  | 2.6718 | 3.0162 | 3.1882 | 3.2685 | 3.8456 | 6.2746 | N/A | N/A
Arkansas | A/C | Rebuild | Single | ArkansasA/CRebuildSingle |  | 1.5979 | 1.7725 | 1.8518 | 1.8788 | 1.9517 | N/A | N/A | N/A
Illinois | A/C | Rebuild | Single | IllinoisA/CRebuildSingle |  | 1.5979 | 1.7725 | 1.8518 | 1.8788 | 1.9517 | N/A | N/A | N/A
Indiana | A/C | Rebuild | Single | IndianaA/CRebuildSingle |  | 1.5979 | 1.7725 | 1.8518 | 1.8788 | 1.9517 | N/A | N/A | N/A
Iowa | A/C | Rebuild | Single | IowaA/CRebuildSingle |  | 1.5979 | 1.7725 | 1.8518 | 1.8788 | 1.9517 | N/A | N/A | N/A
Kentucky | A/C | Rebuild | Single | KentuckyA/CRebuildSingle |  | 1.5979 | 1.7725 | 1.8518 | 1.8788 | 1.9517 | N/A | N/A | N/A
Louisiana | A/C | Rebuild | Single | LouisianaA/CRebuildSingle |  | 1.5979 | 1.7725 | 1.8518 | 1.8788 | 1.9517 | N/A | N/A | N/A
Michigan | A/C | Rebuild | Single | MichiganA/CRebuildSingle |  | 1.5979 | 1.7725 | 1.8518 | 1.8788 | 1.9517 | N/A | N/A | N/A
Minnesota | A/C | Rebuild | Single | MinnesotaA/CRebuildSingle |  | 1.5979 | 1.7725 | 1.8518 | 1.8788 | 1.9517 | N/A | N/A | N/A
Mississippi | A/C | Rebuild | Single | MississippiA/CRebuildSingle |  | 1.5979 | 1.7725 | 1.8518 | 1.8788 | 1.9517 | N/A | N/A | N/A
Missouri | A/C | Rebuild | Single | MissouriA/CRebuildSingle |  | 1.5979 | 1.7725 | 1.8518 | 1.8788 | 1.9517 | N/A | N/A | N/A
Montana | A/C | Rebuild | Single | MontanaA/CRebuildSingle |  | 1.5979 | 1.7725 | 1.8518 | 1.8788 | 1.9517 | N/A | N/A | N/A
North Dakota | A/C | Rebuild | Single | North DakotaA/CRebuildSingle |  | 1.5979 | 1.7725 | 1.8518 | 1.8788 | 1.9517 | N/A | N/A | N/A
South Dakota | A/C | Rebuild | Single | South DakotaA/CRebuildSingle |  | 1.5979 | 1.7725 | 1.8518 | 1.8788 | 1.9517 | N/A | N/A | N/A
Texas | A/C | Rebuild | Single | TexasA/CRebuildSingle |  | 1.5979 | 1.7725 | 1.8518 | 1.8788 | 1.9517 | N/A | N/A | N/A
Wisconsin | A/C | Rebuild | Single | WisconsinA/CRebuildSingle |  | 1.5979 | 1.7725 | 1.8518 | 1.8788 | 1.9517 | N/A | N/A | N/A
Arkansas | A/C | Rebuild | Double | ArkansasA/CRebuildDouble |  | 2.3643 | 2.6704 | N/A | N/A | N/A | N/A | N/A | N/A
Illinois | A/C | Rebuild | Double | IllinoisA/CRebuildDouble |  | 2.3643 | 2.6704 | N/A | N/A | N/A | N/A | N/A | N/A
Indiana | A/C | Rebuild | Double | IndianaA/CRebuildDouble |  | 2.3643 | 2.6704 | N/A | N/A | N/A | N/A | N/A | N/A
Iowa | A/C | Rebuild | Double | IowaA/CRebuildDouble |  | 2.3643 | 2.6704 | N/A | N/A | N/A | N/A | N/A | N/A
Kentucky | A/C | Rebuild | Double | KentuckyA/CRebuildDouble |  | 2.3643 | 2.6704 | N/A | N/A | N/A | N/A | N/A | N/A
Louisiana | A/C | Rebuild | Double | LouisianaA/CRebuildDouble |  | 2.3643 | 2.6704 | N/A | N/A | N/A | N/A | N/A | N/A
Michigan | A/C | Rebuild | Double | MichiganA/CRebuildDouble |  | 2.3643 | 2.6704 | N/A | N/A | N/A | N/A | N/A | N/A
Minnesota | A/C | Rebuild | Double | MinnesotaA/CRebuildDouble |  | 2.3643 | 2.6704 | N/A | N/A | N/A | N/A | N/A | N/A
Mississippi | A/C | Rebuild | Double | MississippiA/CRebuildDouble |  | 2.3643 | 2.6704 | N/A | N/A | N/A | N/A | N/A | N/A
Missouri | A/C | Rebuild | Double | MissouriA/CRebuildDouble |  | 2.3643 | 2.6704 | N/A | N/A | N/A | N/A | N/A | N/A
Montana | A/C | Rebuild | Double | MontanaA/CRebuildDouble |  | 2.3643 | 2.6704 | N/A | N/A | N/A | N/A | N/A | N/A
North Dakota | A/C | Rebuild | Double | North DakotaA/CRebuildDouble |  | 2.3643 | 2.6704 | N/A | N/A | N/A | N/A | N/A | N/A
South Dakota | A/C | Rebuild | Double | South DakotaA/CRebuildDouble |  | 2.3643 | 2.6704 | N/A | N/A | N/A | N/A | N/A | N/A
Texas | A/C | Rebuild | Double | TexasA/CRebuildDouble |  | 2.3643 | 2.6704 | N/A | N/A | N/A | N/A | N/A | N/A
Wisconsin | A/C | Rebuild | Double | WisconsinA/CRebuildDouble |  | 2.3643 | 2.6704 | N/A | N/A | N/A | N/A | N/A | N/A
Arkansas | A/C | Reconductor | Single | ArkansasA/CReconductorSingle |  | 0.4067 | 0.47594 | 0.47958 | 0.48191 | 0.48191 | 0.757 | 1.0528 | 1.457
Illinois | A/C | Reconductor | Single | IllinoisA/CReconductorSingle |  | 0.4067 | 0.47594 | 0.47958 | 0.48191 | 0.48191 | 0.757 | 1.0528 | 1.457
Indiana | A/C | Reconductor | Single | IndianaA/CReconductorSingle |  | 0.4067 | 0.47594 | 0.47958 | 0.48191 | 0.48191 | 0.757 | 1.0528 | 1.457
Iowa | A/C | Reconductor | Single | IowaA/CReconductorSingle |  | 0.4067 | 0.47594 | 0.47958 | 0.48191 | 0.48191 | 0.757 | 1.0528 | 1.457
Kentucky | A/C | Reconductor | Single | KentuckyA/CReconductorSingle |  | 0.4067 | 0.47594 | 0.47958 | 0.48191 | 0.48191 | 0.757 | 1.0528 | 1.457
Louisiana | A/C | Reconductor | Single | LouisianaA/CReconductorSingle |  | 0.4067 | 0.47594 | 0.47958 | 0.48191 | 0.48191 | 0.757 | 1.0528 | 1.457
Michigan | A/C | Reconductor | Single | MichiganA/CReconductorSingle |  | 0.4067 | 0.47594 | 0.47958 | 0.48191 | 0.48191 | 0.757 | 1.0528 | 1.457
Minnesota | A/C | Reconductor | Single | MinnesotaA/CReconductorSingle |  | 0.4067 | 0.47594 | 0.47958 | 0.48191 | 0.48191 | 0.757 | 1.0528 | 1.457
Mississippi | A/C | Reconductor | Single | MississippiA/CReconductorSingle |  | 0.4067 | 0.47594 | 0.47958 | 0.48191 | 0.48191 | 0.757 | 1.0528 | 1.457
Missouri | A/C | Reconductor | Single | MissouriA/CReconductorSingle |  | 0.4067 | 0.47594 | 0.47958 | 0.48191 | 0.48191 | 0.757 | 1.0528 | 1.457
Montana | A/C | Reconductor | Single | MontanaA/CReconductorSingle |  | 0.4067 | 0.47594 | 0.47958 | 0.48191 | 0.48191 | 0.757 | 1.0528 | 1.457
North Dakota | A/C | Reconductor | Single | North DakotaA/CReconductorSingle |  | 0.4067 | 0.47594 | 0.47958 | 0.48191 | 0.48191 | 0.757 | 1.0528 | 1.457
South Dakota | A/C | Reconductor | Single | South DakotaA/CReconductorSingle |  | 0.4067 | 0.47594 | 0.47958 | 0.48191 | 0.48191 | 0.757 | 1.0528 | 1.457
Texas | A/C | Reconductor | Single | TexasA/CReconductorSingle |  | 0.4067 | 0.47594 | 0.47958 | 0.48191 | 0.48191 | 0.757 | 1.0528 | 1.457
Wisconsin | A/C | Reconductor | Single | WisconsinA/CReconductorSingle |  | 0.4067 | 0.47594 | 0.47958 | 0.48191 | 0.48191 | 0.757 | 1.0528 | 1.457
Arkansas | HVDC | New | Single | ArkansasHVDCNewSingle | [9 empty] | 2.4248 | 2.8727 | 3.0174 | 3.2114 | 5.7606
Illinois | HVDC | New | Single | IllinoisHVDCNewSingle | [9 empty] | 2.4525 | 2.911 | 3.0599 | 3.2572 | 5.8085
Indiana | HVDC | New | Single | IndianaHVDCNewSingle | [9 empty] | 2.3308 | 2.7426 | 2.8728 | 3.056 | 5.598
Iowa | HVDC | New | Single | IowaHVDCNewSingle | [9 empty] | 2.4137 | 2.8574 | 3.0003 | 3.1931 | 5.7415
Kentucky | HVDC | New | Single | KentuckyHVDCNewSingle | [9 empty] | 2.5587 | 3.0581 | 3.2233 | 3.4328 | 5.9924
Louisiana | HVDC | New | Single | LouisianaHVDCNewSingle | [9 empty] | 2.8103 | 3.4065 | 3.6105 | 3.849 | 6.4279
Michigan | HVDC | New | Single | MichiganHVDCNewSingle | [9 empty] | 2.5242 | 3.0103 | 3.1703 | 3.3758 | 5.9327
Minnesota | HVDC | New | Single | MinnesotaHVDCNewSingle | [9 empty] | 2.5045 | 2.983 | 3.14 | 3.3432 | 5.8986
Mississippi | HVDC | New | Single | MississippiHVDCNewSingle | [9 empty] | 2.794 | 3.3839 | 3.5853 | 3.822 | 6.3996
Missouri | HVDC | New | Single | MissouriHVDCNewSingle | [9 empty] | 2.3826 | 2.8143 | 2.9525 | 3.1416 | 5.6876
Montana | HVDC | New | Single | MontanaHVDCNewSingle | [9 empty] | 2.1829 | 2.5378 | 2.6453 | 2.8114 | 5.342
North Dakota | HVDC | New | Single | North DakotaHVDCNewSingle | [9 empty] | 2.2336 | 2.608 | 2.7233 | 2.8952 | 5.4298
South Dakota | HVDC | New | Single | South DakotaHVDCNewSingle | [9 empty] | 2.2317 | 2.6054 | 2.7203 | 2.8921 | 5.4265
Texas | HVDC | New | Single | TexasHVDCNewSingle | [9 empty] | 2.6937 | 3.245 | 3.4311 | 3.6561 | 6.2261
Wisconsin | HVDC | New | Single | WisconsinHVDCNewSingle | [9 empty] | 2.674 | 3.1952 | 3.3676 | 3.5864 | 6.2646
Illinois | Sub |  | Upgrade - Add one position (straight or ring bus) |  |  | 1.3189 | 1.5282 | 1.7183 | 1.9084 | 2.2396 | 3.5581 | 5.4814 | 18.3689
Illinois | Sub |  | Upgrade - Add one position (breaker-and-a-half bus) |  |  | 1.8156 | 2.1146 | 2.3875 | 2.6595 | 3.1586 | 5.144 | 7.66 | 23.1721
Illinois | Sub |  | Upgrade - Add one position (double-breaker bus) |  |  | 2.0492 | 2.3836 | 2.6893 | 2.9899 | 3.5177 | 5.5931 | 8.2991 | 23.978
Illinois | Sub |  | Upgrade - Add two positions (straight or ring bus) |  |  | 2.6285 | 3.0461 | 3.4253 | 3.8041 | 4.4651 | 7.0991 | 10.9399 | 28.074
Illinois | Sub |  | Upgrade - Add two positions (breaker-and-a-half bus) |  |  | 3.2765 | 3.7984 | 4.2748 | 4.7502 | 5.5937 | 8.9404 | 13.499 | 33.3523
Illinois | Sub |  | Upgrade - Add two positions (double-breaker bus) |  |  | 4.0891 | 4.7568 | 5.3672 | 5.9672 | 7.0213 | 11.1691 | 16.5753 | 39.2922
Illinois | Sub |  | New - 3 positions (ring bus) |  |  | 8.407 | 9.3093 | 10.168 | 11.0021 | 12.2564 | 17.7023 | 25.6877 | 49.1487
Illinois | Sub |  | New - 3 positions (breaker-and-a-half bus) |  |  | 10.2446 | 11.4363 | 12.5671 | 13.6718 | 15.3939 | 22.5021 | 32.8763 | 62.4021
Illinois | Sub |  | New - 3 positions (double-breaker bus) |  |  | 11.5962 | 12.9842 | 14.3019 | 15.5884 | 17.5783 | 25.8515 | 38.2734 | 72.5783
Illinois | Sub |  | New - 4 positions (ring bus) |  |  | 9.1413 | 10.163 | 11.1268 | 12.0742 | 13.5828 | 19.9234 | 28.9191 | 56.0419
Illinois | Sub |  | New - 4 positions (breaker-and-a-half bus) |  |  | 11.013 | 12.326 | 13.5638 | 14.7837 | 16.762 | 24.7744 | 36.1675 | 69.37
Illinois | Sub |  | New - 4 positions (double-breaker bus) |  |  | 12.7441 | 14.3304 | 15.8253 | 17.2963 | 19.6977 | 29.5057 | 43.4225 | 83.949
Illinois | Sub |  | New - 5 positions (double-breaker bus) |  |  | 10.7794 | 12.0359 | 13.2177 | 14.3872 | 16.2588 | 23.8157 | 35.053 | 66.5737
Illinois | Sub |  | New - 5 positions (breaker-and-a-half bus) |  |  | 13.265 | 14.8931 | 16.5104 | 18.0249 | 20.5248 | 30.6725 | 45.2959 | 87.0906
Illinois | Sub |  | New - 5 positions (double-breaker bus) |  |  | 15.3469 | 17.3625 | 19.1721 | 21.0452 | 23.9874 | 35.8852 | 53.3182 | 101.8833
Illinois | Sub |  | New - 6 positions (ring bus) |  |  | 11.5136 | 12.8895 | 14.1764 | 15.4592 | 17.5852 | 26.0368 | 38.2844 | 73.4669
Illinois | Sub |  | New - 6 positions (breaker-and-a-half bus) |  |  | 14.0334 | 15.7828 | 17.5071 | 19.1369 | 21.8929 | 32.9448 | 48.5871 | 94.0585
Illinois | Sub |  | New - 6 positions (double-breaker bus) |  |  | 16.4948 | 18.7087 | 20.6955 | 22.7531 | 26.1068 | 39.5394 | 58.4673 | 113.254
| Sub |  | HVDC - Line Commutated Converter | [10 empty] | 128.6532 | 383.8443 | 517.8821 | 623.2663 | 776.4463
| Sub |  | HVDC - Voltage Source Converter | [10 empty] | 171.9223 | 498.6515 | 670.1891 | 810.9577 | 987.1107
| Sub |  | Transformer secondary voltage (if applicable) |  |  | 1.8156 | 2.1146 | 2.3875 | 2.6595 | 3.1586 | 5.144 | 7.66 | 23.1721
Note: Transformer unit cost; +10% overhead, +30% Contingency, +7.5% AFUDC | Sub |  | Transformer | 69 kV |  | 9307.6479 | 7576.887 | 8384.5754 | 8826.881 | 9788.4149 | 12019.1735 | 15499.9261 | 21807.5884
| Sub |  | Transformer | 115 kV |  | 7576.887 | 10307.6432 | 8384.5754 | 8826.881 | 9788.4149 | 11423.0225 | 14019.1639 | 17942.2222
| Sub |  | Transformer | 138 kV |  | 8384.5754 | 8384.5754 | 11423.0225 | 9307.6479 | 9788.4149 | 11423.0225 | 14019.1639 | 17942.2222
| Sub |  | Transformer | 161 kV |  | 8826.881 | 8826.881 | 9307.6479 | 12653.7858 | 10307.6432 | 12019.1735 | 14749.9297 | 17942.2222
| Sub |  | Transformer | 230 kV |  | 9788.4149 | 9788.4149 | 9788.4149 | 10307.6432 | 14019.1639 | 12019.1735 | 14749.9297 | 17942.2222
| Sub |  | Transformer | 345 kV |  | 12019.1735 | 11423.0225 | 11423.0225 | 12019.1735 | 12019.1735 | 17076.8417 | 15499.9261 | 18826.8333
| Sub |  | Transformer | 500 kV |  | 15499.9261 | 14019.1639 | 14019.1639 | 14749.9297 | 14749.9297 | 15499.9261 | 22884.5063 | 20769.1318
| Sub |  | Transformer | 765 kV |  | 21807.5884 | 17942.2222 | 17942.2222 | 17942.2222 | 17942.2222 | 18826.8333 | 20769.1318 | 30672.9307
| Sub |  | Transformer | ± 250 kV
| Sub |  | Transformer | ± 400 kV
| Sub |  | Transformer | ± 500 kV
| Sub |  | Transformer | ± 600 kV
[7 empty] | Transformer MVA: |  | 400
List | [8 empty] | 4807669.39
New / Rebuild / Reconductor: | [8 empty] | 2659487.758
New | [8 empty] | 5144042.2746
Rebuild | [8 empty] | 12611199.4226
Reconductor

## Costs over time estimate
MISO
Transmission Line - 5 year construction - convert present year capital cost to nominal cost
Input cells-teal color
Construction cost spend per year allocation
State |  |  | Iowa |  | Year 1 | Year 2 | Year 3 | Year 4 | Year 5
Inflation Rate |  |  | 2.5% |  | 1% | 4% | 35% | 35% | 25%
Project Cost (PC) Present Year |  |  | 100000000 |  | 1000000 | 4000000 | 35000000 | 35000000 | 25000000
Contingency |  | 20% | 20000000 |  | 200000 | 800000 | 7000000 | 7000000 | 5000000
AFUDC |  | 7.5% | 16173781.8926 |  | 45000 | 273375 | 2048878.125 | 5352543.9844 | 8453984.7832
Total Capital Cost |  |  | 136173781.8926 |  | 1245000 | 5073375 | 44048878.125 | 47352543.9844 | 38453984.7832
PI to In Service cost "Nominal" |  |  | 149817666.1599 |  | 1276125 | 5330214.6094 | 47435823.8946 | 52268348.4538 | 43507154.2021
|  | % increase from current year $ | 10.02%
|  | AFUDC effective % | 13.48% |  | AFUDC is calculated based on the average spend for the current year plus the cumulative spend from prior years.
7.1%
Year # | Gross Plant Project Cost ISD Yr.$ (PI) | Net Plant Project Cost ISD Yr.$ (PI) | Annual Depreciation Factor | Return Factor subject to decrease in net plant | Expense Factor | Annual Cost to be Recovered | Present Value Discount Rate | Net Present Value Cost
MTEP Year | [6 empty] | 1
1 | [6 empty] | 0.93371
2 | [6 empty] | 0.87181
3 | [6 empty] | 0.81401
4 | [6 empty] | 0.76005
5 |  |  |  | 8.443% |  |  | 0.70966
6 | 149817666.1599 | 146072224.5059 | 2.5% | 8.232% | 3.425% | 21209971.2207 | 0.66262 | 14054106.9533
7 | 149817666.1599 | 142326782.8519 | 2.5% | 8.021% | 3.425% | 20893726.3544 | 0.61869 | 12926757.6458
8 | 149817666.1599 | 138581341.1979 | 2.5% | 7.81% | 3.425% | 20577481.488 | 0.57768 | 11887114.6925
9 | 149817666.1599 | 134835899.5439 | 2.5% | 7.599% | 3.425% | 20261236.6217 | 0.53938 | 10928503.8857
10 | 149817666.1599 | 131090457.8899 | 2.5% | 7.388% | 3.425% | 19944991.7553 | 0.50362 | 10044750.4759
11 | 149817666.1599 | 127345016.2359 | 2.5% | 7.177% | 3.425% | 19628746.889 | 0.47024 | 9230142.2824
12 | 149817666.1599 | 123599574.5819 | 2.5% | 6.966% | 3.425% | 19312502.0227 | 0.43906 | 8479395.4993
13 | 149817666.1599 | 119854132.9279 | 2.5% | 6.755% | 3.425% | 18996257.1563 | 0.40996 | 7787623.0031
14 | 149817666.1599 | 116108691.2739 | 2.5% | 6.544% | 3.425% | 18680012.29 | 0.38278 | 7150304.979
15 | 149817666.1599 | 112363249.6199 | 2.5% | 6.333% | 3.425% | 18363767.4236 | 0.3574 | 6563261.6985
16 | 149817666.1599 | 108617807.9659 | 2.5% | 6.122% | 3.425% | 18047522.5573 | 0.33371 | 6022628.2924
17 | 149817666.1599 | 104872366.3119 | 2.5% | 5.91% | 3.425% | 17731277.6909 | 0.31159 | 5524831.3738
18 | 149817666.1599 | 101126924.6579 | 2.5% | 5.699% | 3.425% | 17415032.8246 | 0.29093 | 5066567.3767
19 | 149817666.1599 | 97381483.0039 | 2.5% | 5.488% | 3.425% | 17098787.9583 | 0.27164 | 4644782.4856
20 | 149817666.1599 | 93636041.3499 | 2.5% | 5.277% | 3.425% | 16782543.0919 | 0.25364 | 4256654.0406
21 | 149817666.1599 | 89890599.6959 | 2.5% | 5.066% | 3.425% | 16466298.2256 | 0.23682 | 3899573.3103
22 | 149817666.1599 | 86145158.0419 | 2.5% | 4.855% | 3.425% | 16150053.3592 | 0.22112 | 3571129.5325
23 | 149817666.1599 | 82399716.3879 | 2.5% | 4.644% | 3.425% | 15833808.4929 | 0.20646 | 3269095.1311
24 | 149817666.1599 | 78654274.7339 | 2.5% | 4.433% | 3.425% | 15517563.6266 | 0.19278 | 2991412.023
25 | 149817666.1599 | 74908833.0799 | 2.5% | 4.222% | 3.425% | 15201318.7602 | 0.18 | 2736178.9354
141034813.6168

## Cost over time data
Expense Factor and Return Factor (by State)
State | Expense Factor | Return Factor
Arkansas | 2.961% | 8.1%
Illinois | 3.69% | 8.288%
Indiana | 3.16% | 8.225%
Iowa | 3.425% | 8.443%
Kentucky | 3.082% | 8.069%
Louisiana | 2.756% | 8.194%
Michigan | 3.624% | 8.069%
Minnesota | 3.28% | 8.306%
Mississippi | 2.961% | 8.007%
Missouri | 3.196% | 8.085%
Montana | 3.148% | 8.116%
North Dakota | 3.503% | 8.019%
South Dakota | 3.419% | 7.695%
Texas | 3.738% | 7.695%
Wisconsin | 3.708% | 8.188%
Average | 3.31% | 8.1%